AQMD CNG Station Refueling Equipment

Performance Specifications

1.  Fuel Delivery
      5 GEG gal per min / hose   500 GEG gal/per 2 hour window


200 GEG in storage   4 new ASME vessels + 1 existing sphere 


175 GEG/hr ~ 350 scfm  compressor

    
6 vehicles per hour / hose  2 dispensers w/ 6 hoses ~ 24 veh/hr 

       Design for future 2 hose dispenser for total 36 veh/hour


Max fill pressure - 3,600 psi @ 70o F. 

2.  Gas Quality
     Lube oil content < 0.5 pounds per MMscf (10ppm)

     at the compressor skid discharge.

         Water content < 0.5 pounds per MMscf (-100F   

     @ 3,600 psig) at the dryer discharge.

         Odorant level - gas detectable > 1/5 LEL. 

3.  Operations
     Operational and Available to deliver fuel to customers

     99% of the time.  Maximum downtime twelve-month

     period < 90 total hours.

4.  Overall O/M costs < 12c / CNG GEG incl electrical costs.

      (Volume dependent-base on 1000 GEG/day start)

5. Local service < 2 hours of emergency call. 

Parts 12 month warranty period.  Spare parts must be 

     available < 24 hours.

6. Noise level < 75 dba / compressor skid

7.  Minimum liquid and vapor fugitive emissions
