Implementation Assessment Report on Ultra-Low NOx Burners subject to Rules 1146 and 1146.1
Attachment


SOUTH COAST AIR QUALITY MANAGEMENT DISTRICT


Staff Report
Implementation Assessment Report on Ultra-Low NOx Burners subject to Rules 1146 and 1146.1
June 2010
Deputy Executive Officer
Planning, Rule Development, and Area Sources
Elaine Chang, Dr. PH

Assistant Deputy Executive Officer
Planning, Rule Development, and Area Sources
Laki Tisopulos, Ph.D., P.E.

Planning and Rules Manager
Planning, Rule Development, and Area Sources 
Joseph Cassmassi

Author:
Wayne Barcikowski – Air Quality Specialist
Kevin Orellana - Air Quality Specialist

Reviewed by:
Gary Quinn, P.E. – Program Supervisor

South coast air quality management district
governing board

Chairman:
WILLIAM A. BURKE, Ed.D.
Speaker of the Assembly Appointee

Vice Chairman:
DENNIS YATES

Mayor, City of Chino

Cities of San Bernardino County
MEMBERS:


MICHAEL D. ANTONOVICH


Supervisor, Fifth District


Los Angeles County Representative

MARION ASHLEY

Supervisor, Fifth District

Cities Representative, Riverside County

MICHAEL A. CACCIOTI

Council Member, City of South Pasadena


Cities Representative, Los Angeles County/Eastern Region


BILL CAMPBELL


Supervisor, Third District


Orange County Representative

JOSIE GONZALEZ

Supervisor, Fifth District

San Bernardino County Representative

JANE W. CARNEY


Senate Rules Committee Appointee

RONALD O. LOVERIDGE


Mayor, City of Riverside


Cities Representative, Riverside County


JOSEPH K. LYOU, PH.D.

Governor’s Appointee

JUDITH MITCHELL

Councilmember, Rolling Hills Estates

Cities of Los Angeles County, Western Region

JAN PERRY

Council Member, City of Los Angeles


City of Los Angeles


MIGUEL PULIDO


Mayor, City of Santa Ana


Cities Representative, County of Orange

EXECUTIVE OFFICER:

BARRY R. WALLERSTEIN, D.Env.

Table of Contents

1Introduction


2Ultra Low NOx Burner Systems


2Affected Equipment


3September 2008 Board Resolution


4Public Process


4Availability and Performance of Ultra Low NOx Burners


6Impact of Critical External Factors and Testing Techniques on NOx Measurements


10Conclusions and Recommendations


1Appendix A  List of Boilers and Heaters Achieving 9 ppm NOx Level with Ultra-Low NOx Burners
A-

1Appendix B NOx Continuous Emission Monitoring for Boiler with an Ultra-Low NOx Burner and Flue Gas Recirculation
B-



Introduction
Rules 1146 and 1146.1 regulate emissions of oxides of nitrogen (NOx) and carbon monoxide (CO) from industrial, institutional, and commercial boilers, steam generators, and process heaters.  These rules apply to non-RECLAIM boilers, steam generators, and process heaters with maximum rated heat input capacities between 2 and 5 million Btu per hour (Rule 1146.1) and greater than or equal to 5 million Btu per hour (Rule 1146).
On September 5, 2008 Rules 1146 and 1146.1 were amended.  A significant number of the boilers and heaters were required to lower the NOx emission level for natural gas fired units from 30 to 9 ppm (sealed burners
).  The preferred means to comply with these new limits is retrofitting the boiler or heater with ultra low NOx burner (ULNB) systems.
The estimated cost-effectiveness to retrofit the boilers and heaters to the 9 ppm level is as follows:

Table 1 - Cost-effectiveness to retrofit the boilers and heaters to the 9 ppm level as a function of operating capacity
	Category
	Operating Capacity
	Cost Effectiveness

($/ton of NOx reduced)

	20 mmBtu/hr but less than 75 mmBtu/hr 
	100%
	9,600

	
	75%
	10,100

	
	50%
	11,000

	
	25%
	14,000

	5 mmBtu/hr but less than 20 mmBtu/hr 
	100%
	12,400

	
	75%
	13,800

	
	50%
	16,500

	
	25%
	24,900

	Over 2 mmBtu/hr but less than 5 mmBtu/hr 
	100%
	$14,400

	
	75%
	$16,600

	
	50%
	$20,800

	
	25%
	$33,500


Ultra Low NOx Burner Systems

Ultra low NOx burner systems come in a variety of configurations and burner types.  Often, fuel and air are pre-mixed prior to combustion.  This results in a lower and more uniform flame temperature.  Some premix burners also use staged combustion with a fuel rich zone to start combustion and stabilize the flame and a fuel lean zone to complete combustion and reduce the peak flame temperature.  

These burners can also be designed to spread flames over a larger area to reduce hot spots and lower NOx emissions.  Radiant premix burners with ceramic, sintered metal or metal fiber heads spread the flame and produce more radiant heat.  When a burner produces more radiant heat, it results in less heat escaping the boiler through the exhaust gases.  

Most premix burners require the aid of a blower to mix the fuel with air before combustion takes place (primary air).  A commonly used application in combination with these burners is flue gas recirculation (FGR).  FGR recycles a portion of the exhaust stream back into the burner.  Increasing the amount of primary air and/or use of FGR can reduce flame temperature but it also reduces the temperature of combustion gases through dilution and can reduce efficiency.  To maintain efficiency a manufacturer may have to add surface area to the heat exchanger.  Increasing the primary air may also destabilize the flame.  Ultra low NOx burners require sophisticated controls to maintain emissions levels and efficiency, to stabilize the flame, and to maintain a turndown ratio that is sufficient for the demands of the particular operation.
The cutting edge of these control systems has been determined to be 9 ppm (0.011 lbs/106 Btu).  As will be shown later in this report, this NOx limit for both rules can be achieved commercially available systems.

Affected Equipment

Approximately 1,600 units will need to comply with the 9 ppm (0.011 lbs/106 Btu) NOx limit by January 1, 2012 through January 1, 2015.  The applicable compliance date would depend on the unit’s rated heat capacity, number of units at the facility, and type of service (e.g., supplying steam at a university).  These units include those regulated under Rule 1146.1, Group III Rule 1146 units and Group II Rule 1146 units.  Group III includes units burning gaseous fuels, excluding digester and landfill gases, and thermal fluid heaters
 with a rated heat input less than 20 million Btu per hour down to and including 5 million Btu per hour, and all units operated at schools and universities greater than or equal to 5 million Btu per hour (Rule 1146(b)(8)).  Group II includes any unit burning gaseous fuels, excluding digester and landfill gases, with a rated heat input less than 75 million Btu per hour down to and including 20 million Btu per hour, excluding thermal fluid heaters (Rule 1146(b)(7)).  The distribution of the affected equipment is as follows:
Figure 1 – Distribution of Boilers and Heaters subject to the 9 ppm NOx Level

[image: image1.png]Boilers and Heaters sSubject to
9 ppm NOx Limit

# Rule 1146.1 Units
51%

38%

Rule 1146 Group Il
Units

W Rule 1146 Group Il
Units





September 2008 Board Resolution
As previously mentioned, to ensure compliance with the NOx limit, burner manufacturers and installers were required to design ultra low-NOx burners that perform at a level below the 9 ppm level.  However, it was acknowledged that external influences such as fuel heating value and ambient temperature and humidity may hinder the unit from complying with the 9 ppm NOx compliance level on a consistent basis.  
Thus there were challenges that these external influences may cause, not just to boilers subject to this rule, but also other combustion units to fail to comply with their emissions level.  Staff’s expectation that optimization of the burner design in a manner that provides a compliance margin and wider application of positive feedback systems, coupled with the error bands associated with the source test methods, should provide the operators the necessary margin to address such challenges.  
Another concern that was raised during the rulemaking process was availability of ultra low NOx burners that would be required to retrofit the 1,600 affected boilers and heaters.  It was noted in the Rule 1146 and 1146.1 staff reports that there was clear evidence that these types of burners had been successfully retrofitted on boilers and heaters in the San Joaquin Valley Unified Air Pollution Control District (SJVUAPCD) in their Rule 4306.  Source tests conducted in conjunction with Rule 4306 showed a 98% compliance rate with 9 ppm NOx limits using ultra low NOx burners.
Nevertheless, staff, through an adopting resolution committed to continue to work with industry and their interested parties to further study these two issues and report back to the Board prior to the effective dates of the proposed limits and no later than July 15, 2010.  The actual adopting resolution read as follows:
BE IT FURTHER RESOLVED, that the AQMD Governing Board directs staff to conduct an implementation assessment to verify the availability and performance of ultra low NOx burners, and identify and assess the impact of critical external factors and testing techniques on NOx measurements and report back to the Governing Board no later than July 15, 2010
Public Process
Since the amendment of Rules 1146 and 1146.1 in September 2008, AQMD staff has held two Rule Task Force meetings.  The meeting on April 15, 2009 focused on emissions monitoring.  Rule 1146/1146.1 NOx emissions monitoring training classes have been ongoing since April 2009.  To date there have been six training classes with about 565 participants.  The objective of these training classes is to ensure proper application of the portable analyzers when determining compliance with the NOx emission limit.  On June 9, 2010 another Task Force meeting was held to present the information in this report and solicit input.  Subsequent to the Task Force meeting, this report was discussed at the Stationary Source Committee on June 18, 2010.
Availability and Performance of Ultra Low NOx Burners
Staff obtained an updated list of source tests results from the San Joaquin Valley Unified Air Pollution Control District (SJVUAPCD) for boilers and steam generators greater than 5 MMBTU/hr.  This list contained 459 source test results performed for 219 units from September 2002 until March 2010 (See Appendix A).  The NOx compliance limit for these source tests is 9 ppm or less.  The units on this list utilize ULNB or a combination of UNLB’s and Flue Gas Recirculation (FGR).  The sizes of these units range from just above 5 to 260 MMBTU/hr rated heat input capacity.  Units utilizing Selective Catalytic Reduction (SCR) are not included.  
The list includes successive annual tests for units installed beginning in 2002, as well as tests for other units installed more recently.  Out of the 459 source tests performed since September 2002, only 9 results were above 9 ppm (< 2%).  Furthermore, of these 9 exceedances, 4 of the results were within the 10% testing margin of the NOx limit (9.9 ppm).  The testing margin is to account for the accuracy and precision uncertainty of the source test method.  Five out of the 459 test results (or 1%) were above 9.9 ppm.  Every test that exceeded 9 ppm resulted in appropriate corrective actions that eventually resulted in achieving a compliant source test result meeting the 9 ppm NOx limit.  Therefore, each of the 219 units on the list did achieve the 9 ppm NOx compliance limit.  
The types of burners employed in these applications were ultra low NOx burners, with some of them utilizing additional controls, such as Flue Gas Recirculation.  Out of the list in Appendix A, there were ULNB’s from 16 different manufacturers and are listed below:  

	· Alzeta

	· Cleaver Brooks

	· Natcom

	· Industrial Combustion/Profire

	· American Combustion Technology (ACT)

	· ERI

	· Powerflame

	· Micron Fiber-Tech

	· Gideon

	· John Zink

	· Coen

	· Todd

	· Gordon Piatt

	· North American (Magna Flame)

	· URS Corporation

	· Clayton Industries


Some of the companies above have since been acquired by others or have licensed their technology to other companies.  Nonetheless, these ultra low NOx burners have provided compliant test results in the San Joaquin Valley since 2002 until the present time.  
The Best Available Control Technology (BACT) guidelines in the SCAQMD for natural gas-fired boilers above 20 MMBTU/hr call for emissions less than or equal to 9 ppm of NOx (dry corrected to 3% O2) with an ULNB.  These guidelines have been in effect since October 20, 2000.  Since that time, there have been 26 permitted units installed in the South Coast Basin that meet the 9 ppm NOx requirement.  All of these boilers located in the SCAQMD have installed ULNB’s from at least one of the five manufacturers:

	· Alzeta

	· Clayton Industries

	· Cleaver Brooks

	· Coen

· Industrial Combustion


Based on the installations in both the San Joaquin Valley and the SCAQMD, it appears that the ultra low NOx burners have demonstrated the performance requirements to meet the 9 ppm compliance limits set by the BACT guidelines and recently amended District Rules 1146 and 1146.1.  There are several burner manufacturers that have provided compliant ultra low NOx burners to the regulated community, and have thus established availability and performance.  

The focus of this report now turns to the critical external factors that may prevent the ULNB in maintaining the 9 ppm NOx level on a continuous basis during normal operational conditions.
Impact of Critical External Factors and Testing Techniques on NOx Measurements
As discussed previously, several stakeholders during the rule development process expressed concerns about meeting the lower nitrogen oxide limits consistently with ultra low NOx burners.  In particular, these stakeholders were concerned that atmospheric conditions could have a significant impact on NOx emissions from ultra low NOx burners and boilers would not remain in compliance with the new NOx limits.  They were concerned that higher ambient temperatures and associated atmospheric conditions can result in higher concentrations of NOx and that the “margin for error” with the new rule limit and ultra low NOx burners was not sufficient.  It was suggested that a boiler with a new burner that was tuned to operate at or below 9 ppm NOx on a cool morning could be out compliance on the next hot afternoon.  

In order to evaluate the affect of ambient temperature on NOx emissions, staff performed a statistical analysis of one year of data from a non-RECLAIM boiler in the AQMD with a permit emissions limit of 9 ppm NOx that has a continuous emissions monitoring system (CEMS).
The type of ULNB installed with this boiler, and its associated combustion controls, provides efficient operation of the unit while lowering NOx levels.  This ULNB is a premix type burner with multiple fuel zones designed to lower thermal and prompt NOx.  In addition, this burner employs FGR, parallel positioning with O2 Trim, and Variable Frequency Drive (VFD) as added combustion controls.

FGR results in a lower flame temperature which translates into lower NOx emissions.  Parallel positioning, O2 Trim, and VFD serve to control the oxygen level going into the ULNB.  Too little oxygen in the excess air can cause incomplete combustion and could lead to safety issues.  On the other hand, too much oxygen in the excess air often leads to reduced boiler efficiency.  Most boilers are tuned to operate with excess air, but an ideal oxygen level can be sustained with an O2 Trim system.  An O2 Trim system utilizes a sensor in the exhaust that sends a signal to a controller that adjusts the fuel valve and air damper to “trim” the excess oxygen.  Parallel positioning is a type combustion control that, based on boiler steam demand, adjusts both the fuel and air valve actuators simultaneously.  This serves to provide the ULNB with an ideal air/fuel ratio across a range of load conditions.  When parallel positioning is used in conjunction with O2 Trim, there is an added benefit of ideal air/fuel combustion with increased efficiency. 

The ULNB for this boiler also employs the use of a VFD which controls the motor speed on the FD (Forced Draft) fan.  While the fuel valve and air damper are adjusted in parallel, the VFD can adjust the air at the same damper position.  This provides a cost benefit of only using the required energy for the air that needs to be supplied, as opposed to a standard FD fan that runs on a single speed only.  This becomes especially beneficial when smaller quantities of air are required for the ULNB.  

The energy savings of these controls translate into cost savings for these units.  For example, a vendor has presented a 1-2 year payback for a parallel positioning/ O2 Trim system, based on the reduced natural gas fuel consumption.  These types of sophisticated controls work in conjunction with the ULNB to provide a platform of performance at very low NOx levels with the added benefits of increased efficiency for the boiler itself.  

The hourly CEMS, ambient temperature, and relative humidity data is presented in Appendix B.  The results indicate that ambient temperature does not significantly impact emissions from ultra low NOx burners.  The analysis showed no correlation between NOx emissions and ambient temperature (see Figure 2).  

Figure 2 – CEMS NOx and Ambient Temperature for Ultra Low NOx Burner

[image: image2.png]NOx Reading (ppm)

CEMS NOx vs. Ambient Temperature

*

y=-0.0012x+7.1892

R*=7E-05

20 40 60 80 100 120

Ambient Temperature T (°F)





In addition, while a small fraction of readings from the CEMS unit were above 9 ppm, these levels are not associated with higher temperature (see Figure 3).  Staff was not able to determine how many of the readings above 9 ppm are valid.  That analysis would require information about process operation, equipment calibration and other factors.  However, it is noteworthy that while there is no correlation between emission levels and temperature, none of the readings above 9 ppm occurred at ambient temperatures above 80° Fahrenheit.  A detailed examination of the CEMS data indicates that the vast majority of the readings above 9 ppm occurred in the morning, late afternoon/evening, or in the middle of the night.  This suggests that higher emission levels may be associated with startup, shutdown, shift changes and boiler operators.

The data does show that the ultra low NOx burner and control system in the boiler consistently met the emission limit of 9 ppm.  Of the CEMS readings above 9 ppm, more than half of the data points are within 10% of the emission limit (less than 9.9 ppm).  Emission test and CEMS results in this range are within the accuracy and precision of the test method.  Taking this testing margin into account, the percentage of readings above 9 ppm is less than 0.08% (43 out of 5,739 CEMS readings).  

Figure 3 – CEMS NOx Greater Than 9 ppm and Ambient Temperature 

[image: image3.png]NOx Reading (ppm)

50
45
40
35
30
25
20
15
10

CEMS NOx vs. Ambient Temperature (> 9ppm)

*
v=00412x+943
R*=10.0085
.
oo Soo
4
0 20 40 60 80 100

Ambient Temperature T (°F)





Various graphs depicting NOx readings (ppm) and relative humidity are shown in figures 4 through 6.  Figure 4 shows the relationship between the CEMS NOx readings and the local relative humidity of over 70 percent.  This relative humidity would represent foggy to very wet conditions.
Figure 4 – CEMS NOx and Relative Humidity greater than 70% for Ultra Low NOx Burner
 [image: image4.png]NOx Reading (ppm)

25

20

15

10

CEMS NOx vs. Relative Humidity >70%

. s
y=-0.0149x +7.8804 . . &
R=0.0051 *» * oo
* *
* @
10 20 30 40 50 60 70 80

Relative Humidity (%)





Figure 5 shows the relationship between the CEMS NOx readings and the local relative humidity of less than 10 percent.  This relative humidity would represent very dry conditions such as Santa Ana winds.
Figure 5 – CEMS NOx and Relative Humidity less than 10% for Ultra Low NOx Burner
 [image: image5.png]NOx Reading (ppm)

R R R

CEMS NOx Reading vs. Relative Humidity <10%

v=0.00595+7.4568
R>=0.0036 ¢
*
0 20 40 60 30 100 120

Relative Humidity (%)





This last figure was included as a point of reference for relative humidity between the very moist and dry ambient conditions.
Figure 6 – CEMS NOx and Relative Humidity greater than 50% for Ultra Low NOx Burner
[image: image6.png]NOx Reading (ppm)

CEMS NOx Reading vs. Relative Humidity > 50%

50

45 *

40

35

30 V= -0.0081x+7.9248

25 R*=0.00

20 L2 2

15 > e

10 w
5

0 **v—v—M—‘—”—v—‘

0 20 40 60 80 100 120

Relative Humidity (%)





In all of the above charts there was no apparent correlation between the CEMS readings and the relative humidity.  During the June 9, 2010 Task Force meeting it was suggested that the analysis should also include barometric pressure.  For this particular unit that utilizes FGR, parallel positioning, and O2 Trim, it did not appear that this factor would have any impact on the NOx readings.
Conclusions and Recommendations
Based on the previously mentioned SJVUAPCD source test data the 9 ppm ULNB appears to be both available and performing adequately.  The analysis on the selected boiler equipped with a CEMS indicate some (although infrequent) exceedances in NOx most likely due to improper boiler operator procedures.  On this basis, it is recommended that there should be:
· A greater emphasis on boiler operator training.

· Limited access to burner controls for start up, steam/firing rate and shut down by untrained operators.  Errors by untrained operators often lead to noncompliance.

· More frequent maintenance of boiler burner and control system should be encouraged.

The analysis did indicate that the selected boiler was not affected by ambient temperature or relative humidity.  As previously mentioned, the fact that this boiler was equipped with an FGR and parallel positioning with oxygen trim may have contributed to the reliable performance of the ULNB.  Application of such systems on existing boilers and heaters would fall in with the facility modernization concept that was presented in the 2007 Air Quality Management Plan (AQMP)
.
There may have been a certain degree of uncertainty in ascertaining the impact of external critical factors on a boiler equipped with parallel positioning and O2 Trim.  On this basis, staff is recommending to continue monitoring ULNB installations and source test results for another 12 months and report the findings back to the Task Force.  Particular attention should be focused on the installations in the SJVUAPCD and the possible influence that ambient pressure may have on ULNB’s ability of maintaining the 9 ppm NOx limit.  Through a cooperative effort with this agency it is anticipated that more data can be developed in order to better ascertain the impact of external factors on the performance of 9 ppm UNLBs.
More details on this report’s analysis, including a list of the 9 ppm boilers and heaters in the SJVUAPCD and the CEMS data for the selected boiler in the SCAQMD, are presented in the attached staff report.

Appendix A
List of Boilers and Heaters Achieving 9 ppm NOx Level with Ultra-Low NOx Burners

Appendix B
NOx Continuous Emission Monitoring for Boiler with an Ultra-Low NOx Burner and Flue Gas Recirculation

Appendix A

List of Boilers and Heaters Achieving 9 ppm NOx Level with Ultra-Low NOx Burners
	Equipment Description
	 
	Date of Source Test
	NOx Limit (ppm)
	NOx Result (ppm @3% O2)

	CLEAVER-BROOKS (MODEL CB-700-600-150) BOILER WITH ALZETA 24.5 MMBTU/HR LOW-NOX BURNER
	 
	9/25/2002
	9
	4.5

	CLEAVER-BROOKS (MODEL CB-200-800-150) BOILER WITH ALZETA 24.5 MMBTU/HR LOW-NOX BURNER
	 
	9/25/2002
	9
	5.7

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	6/11/2003
	9
	7.7

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	6/12/2003
	9
	7.4

	CLEAVER-BROOKS (MODEL CB-200-800-150) BOILER WITH ALZETA 24.5 MMBTU/HR LOW-NOX BURNER
	 
	10/16/2003
	9
	5.9

	37.4 MMBTU/HR NATURAL GAS-FIRED BOILER WITH ALZETA LOW NOX BURNER
	 
	12/2/2003
	9
	8.5

	30 MMBTU/HR CLEAVER-BROOKS MODEL #CBLE700800 BOILER SERVED BY A CLEAVER BROOKS MODEL CBLE ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	3/18/2004
	9
	4.4

	61.0 MMBTU/HR CLEAVER BROOKS BOILER EQUIPPED WITH NATURAL GAS OR PROPANE-AIRMIX-FIRED NATCOM HYPER-MIX MODEL P-61-G-26-1519 ULTRA LOW-NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	7/26/2004
	9
	6.6

	67.0 MMBTU/HR CLEAVER BROOKS MODEL DL-60 NATURAL GAS-FIRED BOILER WITH PROPANE AS SUPPLEMENTAL OR BACK-UP FUEL WITH TODD DRMB ULTRA LOW-NOX BURNER AND INDUCED FLUE GAS RECIRCULATION WITH O2 CONTROLLER
	 
	7/26/2004
	9
	6.5

	NEBRASKA MODEL #NS-E-65 BOILER (#6) SERVED BY A 94 MMBTU/HR TODD/RADIAN MODEL RMB ULTRA LOW-NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	9/16/2004
	9
	8.5

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#1) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	10/27/2004
	9
	8.4

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#2) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	10/27/2004
	9
	10.1

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#3) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	10/27/2004
	9
	9.3

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#2) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	11/4/2004
	9
	8.2

	37.4 MMBTU/HR NATURAL GAS-FIRED BOILER WITH ALZETA LOW NOX BURNER
	 
	11/18/2004
	9
	9

	60.6 MMBTU/HR NEBRASKA MODEL NS-C-61-ECON NATURAL GAS FIRED BOILER WITH AN ALZETA MODEL CSB642R-LEA ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	11/19/2004
	9
	3.8

	20.9 MMBTU/HR SUPERIOR MODEL 6-5-2500 BOILER SERVED BY AN AMERICAN COMBUSTION TECHNOLOGY, INC. MODEL SLE-07 ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM 
	 
	1/12/2005
	9
	8.7

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#3) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	2/10/2005
	9
	7.5

	25.3 MMBTU/HR HURST, MODEL NO. SERIES 400, NATURAL GAS/PROPANE-FIRED BOILER WITH AN ALZETA MODEL CSB252-LEA BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	4/14/2005
	9
	5.5

	33.5 MMBTU/HR CLEAVER BROOKS MODEL #CB800 NATURAL GAS-FIRED FIRETUBE BOILER WITH AN ERI MODEL LNRETRO FORCED DRAFT ULTRA LOW-NOX BURNER WITH FLUE GAS RE-CIRCULATION (FGR) AND EQUIPPED WITH A NATURAL GAS FLOW METER
	 
	4/27/2005
	9
	4.9

	24.494 MMBTU/HR CLEAVER BROOKS MODEL CBI 200-600,200 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTI-9 ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	5/16/2005
	9
	8.2

	ONE 20.9 MMBTU/HR CLEAVER BROOKS MODEL CEW LN200-500,150# NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD2106 GA-FO9R ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	5/18/2005
	9
	7.5

	19.95 MMBTU/HR HURST MODEL 54X-500-15 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL NVC-10-G-30 ULTRA-LOW NOX BURNER
	 
	5/20/2005
	9
	6.2

	33.6 MMBTU/HR SUPERIOR MODEL 8-5-400-S150-G-IC NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD336NGX ULTRA LOW NOX BURNER
	 
	5/23/2005
	9
	4.8

	12.6 MMBTU/HR CLEAVER BROOKS MODEL C-B-200-300 NATURAL GAS FIRED BOILER EQUIPPED WITH AN ALZETA MODEL CSB126R LOW NOX BURNER
	 
	5/27/2005
	9
	5.4

	21.0 MMBTU/HR BABCOCK & WILCOX MODEL FM TYPE D NATURAL GAS-FIRED BOILER WITH A POWERFLAME ULTRA LOW NOX NOVA PLUS MODEL NVC10-G-30 BURNER
	 
	5/28/2005
	9
	12.3

	48.58 MMBTU/HR HURST MODEL S4-X-1200-150 NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOK MODEL NTS 504 NGX-FGR ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	5/28/2005
	9
	6

	33.48 MMBTU/HR CLEAVER BROOKS MODEL CB700-800-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL CB(LE9)700-800 BURNER WITH FLUE GAS RECIRCULATION
	 
	5/31/2005
	9
	4.6

	84 MMBTU/HR THERMOTICS NATURAL & TEOR GAS-FIRED STEAM GENERATOR W/ MAGNA FLAME MODEL 4231-85-GLE-X2631 BURNER, FGR, AND RADAC O2 CONTROLLER
	 
	6/1/2005
	9
	7.2

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	6/14/2005
	9
	7.1

	14.65 MMBTU/HR CLEAVER-BROOKS MODEL CEW (LE9) 700-350-150ST NATURAL GAS-FIRED BOILER, WITH A CLEAVER-BROOKS MODEL LTD-147NGX-F9R ULTRA-LOW NOX BURNER
	 
	6/14/2005
	9
	7.8

	21.0 MMBTU/HR BABCOCK & WILCOX MODEL FM TYPE D NATURAL GAS-FIRED BOILER WITH A POWERFLAME ULTRA LOW NOX NOVA PLUS MODEL NVC10-G-30 BURNER
	 
	6/15/2005
	9
	12.6

	21.0 MMBTU/HR BABCOCK & WILCOX MODEL FM TYPE D NATURAL GAS-FIRED BOILER WITH A POWERFLAME ULTRA LOW NOX NOVA PLUS MODEL NVC10-G-30 BURNER
	 
	6/29/2005
	9
	4.3

	33.4 MMBTU/HR CLEAVER-BROOKS MODEL CBLE 700-800-250 NATURAL GAS-FIRED BOILER WITH LOW NOX BURNER
	 
	7/13/2005
	9
	6.6

	33.0 MMBTU/HR CLEAVER-BROOKS (BOILER #1) MODEL CB 200-800 WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9PPM ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	7/29/2005
	9
	7.7

	120.183 MMBTU/HR CLEAVER BROOKS BOILER, MODEL DLDH-102-E, WITH A TODD MODEL D-RMB ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM.  
	 
	8/9/2005
	9
	7

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB200-500 NATURAL GAS-FIRED BOILER WITH FUEL OIL #2 AS A BACK-UP FUEL, AND EQUIPPED WITH CLEAVER BROOKS MODEL CBNT ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	8/11/2005
	9
	7.4

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CEW LN200-500,150# NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD2106 GA-FO9R ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	8/11/2005
	9
	6.8

	20.9 MMBTU/HR CLEAVER-BROOKS MODEL CB 700-500,200# NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOKS MODEL NTI-500 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	9/2/2005
	9
	4.6

	6.27 MMBTU/HR CLEAVER BROOKS MODEL CB200-150-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-150 ULTRA LOW NOX BURNER
	 
	9/15/2005
	9
	4.5

	47.8 MMBTU/HR BABCOCK AND WILCOX NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECH MODEL ACI-04G LOW NOX BURNER WITH INDUCED FLUE GAS RECIRCULATION
	 
	9/16/2005
	9
	10.7

	21.0 MMBTU/HR SUPERIOR MODEL X6X2500S150-M SEMINOLE NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECHNOLOGY INC MODEL ACT 07-SLE ULTRA LOW NOX BURNER
	 
	9/28/2005
	9
	8.6

	19.95 MMBTU/HR CLEAVER-BROOKS MODEL CB-700-500 NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB 22-1S0-30 ULTRA LOW NOX BURNER AND FORCED FLUE GAS RECIRCULATION 
	 
	10/4/2005
	9
	8.9

	19.9 MMBTU/HR JOHNSTON BOILER CO. MODEL PFTA500-4HG200S BOILER #2 WITH AN INDUSTRIAL COMBUSTION MODEL NTD210NGX LOW NOX BURNER
	 
	10/5/2005
	9
	7.5

	28.576 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 200-700-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROODS MODEL CB(LE9) 200-700 ULTRA LOW NOX BURNER
	 
	10/5/2005
	9
	7.7

	29.4 MMBTU/HR HURST MODEL 400 G/P 700-150 NATURAL GAS-FIRED BOILER, WITH PROPANE AS A BACK-UP FUEL, WITH A CLEAVER-BROOKS MODEL NTD294NGX-09S-8P ULTRA LOW NOX BURNER 
	 
	10/12/2005
	9
	5.8

	6.27 MMBTU/HR CLEAVER BROOKS MODEL CB200-150-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-150 ULTRA LOW NOX BURNER
	 
	10/14/2005
	9
	7.6

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	10/17/2005
	9
	9.7

	29.92 MMBTU/HR CLEAVER BROOKS MODEL CB-700-700-200 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL INTEGRAL ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	10/21/2005
	9
	2.3

	21.0 MMBTU/HR SUPERIOR MODEL X6X2500S150-M SEMINOLE NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECHNOLOGY INC MODEL ACT 07-SLE ULTRA LOW NOX BURNER
	 
	10/28/2005
	9
	9

	60.7 MMBTU/HR NEBRASKA MODEL NS-C-61-ECON NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB642R-LEA ULTRA LOW NOX BURNER
	 
	11/2/2005
	9
	5.6

	60.6 MMBTU/HR NEBRASKA MODEL NS-C-61-ECON NATURAL GAS FIRED BOILER WITH AN ALZETA MODEL CSB642R-LEA ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	11/2/2005
	9
	5.6

	60 MMBTU/HR NEBRASKA MODEL NS-F-89 BOILER WITH AN ALZETA MODEL CSB625R ULTRA LOW NOX BURNER
	 
	11/8/2005
	9
	5.3

	47.8 MMBTU/HR BABCOCK AND WILCOX NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECH MODEL ACI-04G LOW NOX BURNER WITH INDUCED FLUE GAS RECIRCULATION
	 
	11/9/2005
	9
	7.6

	20.9 MMBTU/HR CLEAVER BROOKS MODEL 700-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL PROFIRE NT ULTRA LOW NOX BURNER
	 
	11/15/2005
	9
	8.2

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB 1700 500 125 BOILER (NO. 2) WITH A CLEAVER BROOKS MODEL NUMBER NTI-500 LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	11/17/2005
	9
	8.1

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB 1700 500 125 BOILER (NO. 1) WITH A CLEAVER BROOKS MODEL NUMBER NTI-500 LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	11/17/2005
	9
	7.1

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	11/23/2005
	9
	7.6

	63 MMBTU/HR HURST SERIES 400 FIRETUBE NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB630 ULTRA LOW NOX BURNER
	 
	11/29/2005
	9
	4.2

	20.9 MMBTU/HR CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	12/1/2005
	9
	8.7

	20.9 MMBTU/HR  CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER
	 
	12/1/2005
	9
	8.7

	20.9 MMBTU/HR CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	12/1/2005
	9
	8.7

	7.0 MMBTU/HR NATURAL GAS-FIRED UBW MODEL UFS175150 BOILER EQUIPPED WITH A GORDON PIATT MODEL RMB-GO-175 7.0 MMBTU/HR BURNER AND INDUCED FLUE GAS RECIRCULATION 
	 
	12/5/2005
	9
	7.1

	7.0 MMBTU/HR NATURAL GAS-FIRED UBW MODEL UFS175150 BOILER EQUIPPED WITH A GORDON PIATT MODEL RMB-GO-175 7.0 MMBTU/HR BURNER AND INDUCED FLUE GAS RECIRCULATION 
	 
	12/5/2005
	9
	6.9

	11.7 MMBTU/HR CLEAVER BROOKS MODEL CB200X-300-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	12/12/2005
	9
	5.7

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#1) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	12/13/2005
	9
	7.3

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#2) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	12/13/2005
	9
	7.7

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#3) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	12/13/2005
	9
	8

	20.9 MMBTU/HR SUPERIOR MODEL 6-5-2500 BOILER SERVED BY AN AMERICAN COMBUSTION TECHNOLOGY, INC. MODEL SLE-07 ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM 
	 
	12/20/2005
	9
	8.4

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	12/21/2005
	9
	5.3

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	12/21/2005
	9
	7.8

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	12/21/2005
	9
	8.2

	33.6 MMBTU/HR SUPERIOR MODEL #8-5-400-S150-G-IC NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #NTD336NGXF9R ULTRA LOW NOX BURNER
	 
	1/12/2006
	9
	6.7

	25.1 MMBTU/HR  CLEAVER BROOKS MODEL CBLE 700-600-150 NATURAL GAS-FIRED BOILER  WITH A CLEAVER BROOKS MODEL CB NTI-9 PPM ULTRA LOW NOX BURNER
	 
	2/22/2006
	9
	9

	60.7 MMBTU/HR NEBRASKA MODEL NS-C-61-ECON NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB642R-LEA ULTRA LOW NOX BURNER
	 
	2/24/2006
	9
	5.7

	21 MMBTU/HR IRON FIREMAN MODEL 300-777 BOILER WITH AN ALZETA MODEL CSB22-250-30/15 LOW-NOX BURNER
	 
	3/2/2006
	9
	6.4

	25.3 MMBTU/HR HURST, MODEL NO. SERIES 400, NATURAL GAS/PROPANE-FIRED BOILER WITH AN ALZETA MODEL CSB252-LEA BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	3/2/2006
	9
	5

	12.5 MMBTU/HR CLEAVER BROOKS MODEL #CBLE200-300 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CB(LE15) 700-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	3/9/2006
	9
	8.2

	12.6 MMBTU/HR CLEAVER BROOKS MODEL C-B-200-300 NATURAL GAS FIRED BOILER EQUIPPED WITH AN ALZETA MODEL CSB126R LOW NOX BURNER
	 
	4/20/2006
	9
	6.1

	ONE 20.9 MMBTU/HR CLEAVER BROOKS MODEL CEW LN200-500,150# NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD2106 GA-FO9R ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	4/26/2006
	9
	7.1

	60.0 MMBTU/HR MURRAY IRON WORKS MODEL MG4E-25 NATURAL GAS-FIRED BOILER, WITH ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-60 9 PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	5/2/2006
	9
	6.1

	26.0 MMBTU/HR BABCOCK & WILCOX NATURAL GAS-FIRED BOILER WITH AN ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-24 9 PPM ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	5/2/2006
	9
	7.9

	8.4 MMBTU/HR DIXON MODEL SK-10 NATURAL GAS-FIRED BOILER WITH A MICRON FIBER-TECH MODEL MFT11X30 ULTRA LOW NOX BURNER
	 
	5/9/2006
	9
	6.5

	24.494 MMBTU/HR CLEAVER BROOKS MODEL CBI 200-600,200 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTI-9 ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	5/12/2006
	9
	8.7

	19.95 MMBTU/HR HURST MODEL 54X-500-15 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL NVC-10-G-30 ULTRA-LOW NOX BURNER
	 
	5/17/2006
	9
	7.2

	48.58 MMBTU/HR HURST MODEL S4-X-1200-150 NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOK MODEL NTS 504 NGX-FGR ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	5/26/2006
	9
	7.9

	48.58 MMBTU/HR HURST MODEL S4-X-1200-150 NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOK MODEL NTS 504 NGX-FGR ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	5/26/2006
	9
	7.4

	33.5 MMBTU/HR CLEAVER BROOKS MODEL #CB800 NATURAL GAS-FIRED FIRETUBE BOILER WITH AN ERI MODEL LNRETRO FORCED DRAFT ULTRA LOW-NOX BURNER WITH FLUE GAS RE-CIRCULATION (FGR) AND EQUIPPED WITH A NATURAL GAS FLOW METER
	 
	5/26/2006
	9
	6.8

	84 MMBTU/HR THERMOTICS NATURAL & TEOR GAS-FIRED STEAM GENERATOR W/ MAGNA FLAME MODEL 4231-85-GLE-X2631 BURNER, FGR, AND RADAC O2 CONTROLLER
	 
	6/1/2006
	9
	8.5

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	6/8/2006
	9
	8.8

	33.48 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS MODEL CB700-800-150ST BOILER WITH CB(LE9) 700-800 ULTRA LOW NOX BURNER - BOILER #1 
	 
	6/12/2006
	9
	7.6

	33.48 MMBTU/HR CLEAVER BROOKS MODEL CB700-800-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL CB(LE9)700-800 BURNER WITH FLUE GAS RECIRCULATION
	 
	6/12/2006
	9
	7.1

	21.0 MMBTU/HR BABCOCK & WILCOX MODEL FM TYPE D NATURAL GAS-FIRED BOILER WITH A POWERFLAME ULTRA LOW NOX NOVA PLUS MODEL NVC10-G-30 BURNER
	 
	6/15/2006
	9
	4.9

	29.92 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS, MODEL CB-700-700-200, BOILER (NO.2) WITH A CLEAVER BROOKS MODEL NTI-700 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	6/27/2006
	9
	9.7

	73.0 MMBTU/HR NEBRASKA BOILER MODEL NSE-58 NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB770R-LEA ULTRA LOW NOX BURNER.
	 
	6/28/2006
	9
	4.1

	NEBRASKA MODEL NS-F-81 NATURAL GAS OR LPG-FIRED BOILER (WEST) WITH A 97 MMBTU/HR ALZETA MODEL CSB-1210 ULTRA-LOW NOX BURNER
	 
	6/28/2006
	9
	2.8

	NEBRASKA MODEL NS-F-81 NATURAL GAS OR LPG-FIRED BOILER (EAST) WITH A 97 MMBTU/HR ALZETA MODEL CSB-1210 ULTRA-LOW NOX BURNER 
	 
	6/28/2006
	9
	2.3

	43 MMBTU/HR CLEAVER BROOKS MODEL #D-60E (#1) NATURAL GAS-FIRED BOILER WITH FUEL OIL #2 AS BACK-UP FUEL, A CLEAVER BROOKS MODEL NTS420LGS-09S-1P LOW NOX BURNER, AND FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	6/28/2006
	9
	8.4

	26.0 MMBTU/HR BABCOCK & WILCOX NATURAL GAS-FIRED BOILER WITH AN ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-24 9 PPM ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	6/29/2006
	9
	7.3

	72.0 MMBTU/HR BABCOCK & WILCOX MODEL FM-1936 NATURAL GAS- FIRED BOILER, WITH ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-60 9 PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	7/10/2006
	9
	8.2

	33.0 MMBTU/HR CLEAVER-BROOKS (BOILER #1) MODEL CB 200-800 WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9PPM ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	7/14/2006
	9
	7

	32.66 MMBTU/HR CLEAVER-BROOKS MODEL CB200-800, 150# NATURAL GAS-FIRED BOILER #3 WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9 PPM ULTRA-LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM.
	 
	7/14/2006
	9
	7

	32.66 MMBTU/HR CLEAVER-BROOKS (BOILER #2) MODEL CB200-800, 150# NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9PPM ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	7/14/2006
	9
	7.2

	29.92 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS, MODEL CB-700-700-200, BOILER (NO.2) WITH A CLEAVER BROOKS MODEL NTI-700 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	7/14/2006
	9
	6.5

	20.9 MMBTU/HR  CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER
	 
	7/17/2006
	9
	7.4

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB200-500 NATURAL GAS-FIRED BOILER WITH FUEL OIL #2 AS A BACK-UP FUEL, AND EQUIPPED WITH CLEAVER BROOKS MODEL CBNT ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	7/18/2006
	9
	7.3

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CEW LN200-500,150# NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD2106 GA-FO9R ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	7/18/2006
	9
	6.9

	63.0 MMBTU/HR CLEAVER BROOKS, MODEL CBL-700-1500, NATURAL GAS-FIRED BOILER WITH AN INDUSTRIAL COMBUSTION, MODEL NTS2-630, ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	7/21/2006
	9
	7.7

	26.4 MMBTU/HR HURST MODEL S400-700-150 NATURAL GAS-FIRED BOILER WITH A POWER FLAME MODEL NOVA PLUS-NVC12-G-30 ULTRA LOW NOX BURNER WITH INDUCED FGR
	 
	7/27/2006
	9
	3.5

	85 MMBTU/HR BABCOCK & WILCOX MODEL FMD-10 BOILER WITH NATCOM MODEL B-85-G-35-2126 LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM (BOILER #3)
	 
	7/31/2006
	9
	7.8

	33.4 MMBTU/HR CLEAVER-BROOKS MODEL CBLE 700-800-250 NATURAL GAS-FIRED BOILER WITH LOW NOX BURNER
	 
	8/4/2006
	9
	9

	180 MMBTU/HR NEBRASKA BOILER, MODEL NO. N2S-7-95, WITH AN ULTRA LOW NOX TODD RAPID MIX BURNER (RMB) AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM WITH A ROSEMOUNT OXYGEN CONTROLLER.
	 
	8/7/2006
	9
	6.1

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	8/7/2006
	9
	7

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	8/7/2006
	9
	7.2

	34.6 MMBTU/HR ERIE CITY IRON WORKS MODEL TYPE VC BOILER #3 WITH A COEN MODEL QLA 20.0 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	8/9/2006
	9
	8.5

	60.4 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS MODEL DL-60 BOILER WITH TODD ULTRA LOW-NOX DRMB BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	8/9/2006
	9
	7.8

	120.183 MMBTU/HR CLEAVER BROOKS BOILER, MODEL DLDH-102-E, WITH A TODD MODEL D-RMB ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM.  
	 
	8/15/2006
	9
	6.7

	120.183 MMBTU/HR CLEAVER BROOKS BOILER, MODEL DLDH-102-E, WITH A TODD MODEL D-RMB ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM.  
	 
	8/15/2006
	9
	7.6

	85 MMBTU/HR PCL IDENTIFICATION #POSO-J402 NATURAL GAS-FIRED STEAM GENERATOR WITH A NORTH AMERICAN MODEL LE LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR), AND O2 CONTROLLER
	 
	8/18/2006
	8
	8

	20.925 MMBTU/HR HURST MODEL S4-X-500-150# NATURAL GAS-FIRED BOILER WITH AN INDUSTRIAL COMBUSTION MODEL NTD210NGX-09S-6P ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	8/18/2006
	9
	7.9

	25.1 MMBTU/HR CLEAVER BROOKS MODEL CB200-600, 150# PACKAGED FIRE-TUBE NATURAL GAS-FIRED BOILER, WITH ALZETA CSB-252R LOW-NOX BURNERS, AND O2 CONTROLLER
	 
	8/18/2006
	9
	5

	20.9 MMBTU/HR CLEAVER-BROOKS MODEL CB 700-500,200# NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOKS MODEL NTI-500 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	9/6/2006
	9
	7.3

	32.0 MMBTU/HR CLEAVER BROOKS MODEL CB200-800-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL CB (LE9) 700-800 ULTRA LOW NOX BURNER AND INTERNAL BAFFLING FLUE GAS RECIRCULATION SYSTEM - BOILER #2
	 
	9/7/2006
	9
	6.7

	47.8 MMBTU/HR BABCOCK AND WILCOX NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECH MODEL ACI-04G LOW NOX BURNER WITH INDUCED FLUE GAS RECIRCULATION
	 
	9/7/2006
	9
	8.2

	21.0 MMBTU/HR SUPERIOR MODEL X6X2500S150-M SEMINOLE NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECHNOLOGY INC MODEL ACT 07-SLE ULTRA LOW NOX BURNER
	 
	9/8/2006
	9
	9.7

	21.0 MMBTU/HR SUPERIOR MODEL X6X2500S150-M SEMINOLE NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECHNOLOGY INC MODEL ACT 07-SLE ULTRA LOW NOX BURNER
	 
	9/8/2006
	9
	8.4

	CLEAVER-BROOKS (MODEL CB-200-800-150) BOILER WITH ALZETA 24.5 MMBTU/HR LOW-NOX BURNER
	 
	9/14/2006
	9
	6.8

	CLEAVER-BROOKS (MODEL CB-700-600-150) BOILER WITH ALZETA 24.5 MMBTU/HR LOW-NOX BURNER
	 
	9/14/2006
	9
	4.8

	29.4 MMBTU/HR SUPERIOR, MODEL 4-5-3502, NATURAL GAS-FIRED BOILER WITH A POWER FLAME, MODEL NVC-12, ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	9/15/2006
	9
	2.8

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	9/21/2006
	9
	9

	21.0 MMBTU/HR SUPERIOR MODEL X6X2500S150-M SEMINOLE NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECHNOLOGY INC MODEL ACT 07-SLE ULTRA LOW NOX BURNER
	 
	9/26/2006
	9
	8.6

	33.6 MMBTU/HR SUPERIOR MODEL 8-5-400-S150-G-IC NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD336NGX ULTRA LOW NOX BURNER
	 
	9/29/2006
	9
	5.8

	30 MMBTU/HR CLEAVER BROOKS MODEL D-24E (#2) NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD336NGX-F09R LOW NOX BURNER, A FLUE GAS RECIRCULATION (FGR) SYSTEM, AND FUEL OIL #2 AS BACK-UP FUEL
	 
	10/6/2006
	9
	7.5

	25.1 MMBTU/HR CLEAVER BROOKS MODEL CB200-600, 150# PACKAGED FIRE-TUBE NATURAL GAS-FIRED BOILER, WITH ALZETA CSB-252R LOW-NOX BURNERS AND O2 CONTROLLER
	 
	10/9/2006
	9
	7.2

	6.27 MMBTU/HR CLEAVER BROOKS MODEL CB200-150-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-150 ULTRA LOW NOX BURNER
	 
	10/10/2006
	9
	7

	6.27 MMBTU/HR CLEAVER BROOKS MODEL CB200-150-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-150 ULTRA LOW NOX BURNER
	 
	10/10/2006
	9
	6.7

	29.92 MMBTU/HR CLEAVER BROOKS MODEL CB-700-700-200 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL INTEGRAL ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	10/11/2006
	9
	7.9

	11.7 MMBTU/HR CLEAVER BROOKS MODEL CB200X-300-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	10/11/2006
	9
	4.5

	20.9 MMBTU/HR CLEAVER BROOKS MODEL 700-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL PROFIRE NT ULTRA LOW NOX BURNER
	 
	10/17/2006
	9
	8

	19.95 MMBTU/HR CLEAVER-BROOKS MODEL CB-700-500 NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB 22-1S0-30 ULTRA LOW NOX BURNER AND FORCED FLUE GAS RECIRCULATION 
	 
	10/19/2006
	9
	4.9

	60 MMBTU/HR NEBRASKA MODEL NS-F-89 BOILER WITH AN ALZETA MODEL CSB625R ULTRA LOW NOX BURNER
	 
	10/20/2006
	9
	5.5

	20.5 MMBTU/HR CLEAVER BROOKS MODEL CBLE-NIT-500-200ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS NTI MODEL CBLE-700-500-200ST ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	10/24/2006
	9
	8.1

	28.576 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 200-700-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROODS MODEL CB(LE9) 200-700 ULTRA LOW NOX BURNER
	 
	11/2/2006
	9
	7.6

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	11/3/2006
	9
	5.6

	29.4 MMBTU/HR HURST MODEL 400 G/P 700-150 NATURAL GAS-FIRED BOILER, WITH PROPANE AS A BACK-UP FUEL, WITH A CLEAVER-BROOKS MODEL NTD294NGX-09S-8P ULTRA LOW NOX BURNER 
	 
	11/6/2006
	9
	8.3

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#1) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	11/16/2006
	9
	5.7

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#2) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	11/16/2006
	9
	7.6

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#3) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	11/16/2006
	9
	8.1

	11.0 MMBTU/HR TEJAS, TRIPLE S MODEL NATURAL GAS-FIRED BOILER, WITH AN INDUSTRIAL COMBUSTION MODEL NTH110NG-09S-4P ULTRA LOW NOX BURNER, AND INDUCED FGR
	 
	11/17/2006
	9
	8

	48 MMBTU/HR CLEAVER BROOKS MODEL D-60 NATURAL GAS-FIRED BOILER WITH CLEAVER BROOKS MODEL PROFIRE NTS LOW NOX BURNER 
	 
	11/28/2006
	9
	7.5

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB 1700 500 125 BOILER (NO. 2) WITH A CLEAVER BROOKS MODEL NUMBER NTI-500 LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	12/11/2006
	9
	6.4

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB 1700 500 125 BOILER (NO. 1) WITH A CLEAVER BROOKS MODEL NUMBER NTI-500 LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	12/11/2006
	9
	7.5

	50.0 MMBTU/HR NEBRASKA BOILER MODEL #NS-D-49 WITH A NATCOM MODEL ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	12/15/2006
	9
	7.6

	7.0 MMBTU/HR NATURAL GAS-FIRED UBW MODEL UFS175150 BOILER EQUIPPED WITH A GORDON PIATT MODEL RMB-GO-175 7.0 MMBTU/HR BURNER AND INDUCED FLUE GAS RECIRCULATION 
	 
	12/18/2006
	9
	8.7

	75.6 MMBTU/HR SUPERIOR MODEL SEMINOLE 3 PASS, OR EQUIVALENT, NATURAL GAS-FIRED BOILER #1 WITH AN ALZETA MODEL CSB 756, OR EQUIVALENT, ULTRA LOW-NOX BURNER, AND FORCED FLUE GAS RECIRCULATION
	 
	12/19/2006
	9
	4.5

	75.6 MMBTU/HR SUPERIOR MODEL SEMINOLE 3 PASS, OR EQUIVALENT, NATURAL GAS-FIRED BOILER #2 WITH AN ALZETA MODEL CSB 756, OR EQUIVALENT, ULTRA LOW-NOX BURNER, AND FORCED FLUE GAS RECIRCULATION
	 
	12/19/2006
	9
	5.3

	12.6 MMBTU/HR NATURAL GAS FIRED WHIRLPOWER SPACE CONDITIONER BOILER WITH A POWERFLAME MODEL NVC-7-G-30 ULTRA-LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	12/20/2006
	9
	6.3

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	12/21/2006
	9
	7.5

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	12/21/2006
	9
	8.3

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	12/21/2006
	9
	7.4

	21 MMBTU/HR IRON FIREMAN MODEL 300-777 BOILER WITH AN ALZETA MODEL CSB22-250-30/15 LOW-NOX BURNER
	 
	2/22/2007
	9
	5.9

	37.8 MMBTU/HR HURST MODEL SERIES 500 NATURAL GAS/YELLOW GREASE-FIRED BOILER EQUIPPED WITH JOHN ZINC/GORDON PIATT ULTRA LOW-NOX BURNER MODEL RMB-GO-90-E2-30-F9H WITH FORCED FGR
	 
	3/1/2007
	9
	8.2

	60.7 MMBTU/HR NEBRASKA MODEL NS-C-61-ECON NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB642R-LEA ULTRA LOW NOX BURNER
	 
	3/2/2007
	9
	5.4

	21.0 MMBTU/HR NATURAL GAS-FIRED PACKAGE BOILER WITH A JOHN ZINK ULTRA LOW NOX BURNER AND FGR
	 
	3/5/2007
	9
	5.7

	ONE 34.6 MMBTU/HR ERIE CITY IRON WORKS MODEL TYPE VC BOILER #2 WITH A COEN MODEL ULN ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	3/5/2007
	9
	7.6

	20.9 MMBTU/HR CLEAVER BROOKS MODEL FIRETUBE 4WG700-500 200 BOILER WITH INDUSTRIAL COMBUSTION MODEL PROFIRE ULTRA LOW NOX BURNER INCLUDING FLUE GAS RECIRCULATION SYSTEM AND O2 CONTROLLER.
	 
	3/9/2007
	9
	6.4

	28.5 MMBTU/HR HURST MODEL 400 G/P 700-150 NATURAL GAS-FIRED BOILER  SERVED BY A CLEAVER BROOKS MODEL NTD294NGX-095-8P ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR) SYSTEM WITH PROPANE AS BACKUP FUEL
	 
	3/20/2007
	9
	7.2

	14.65 MMBTU/HR CLEAVER-BROOKS MODEL CEW (LE9) 700-350-150ST NATURAL GAS-FIRED BOILER, WITH A CLEAVER-BROOKS MODEL LTD-147NGX-F9R ULTRA-LOW NOX BURNER
	 
	3/20/2007
	9
	8.9

	28.6 MMBTU/HR CLEAVER-BROOKS MODEL CB-700 SYSTEM 20 NATURAL GAS/PROPANE-FIRED BOILER WITH A CLEAVER-BROOKS MODEL NTI-15-700 ULTRA LOW NOX BURNER, FGR, AND O2 TRIM SYSTEM
	 
	3/27/2007
	9
	5.9

	25.1 MMBTU/HR  CLEAVER BROOKS MODEL CBLE 700-600-150 NATURAL GAS-FIRED BOILER  WITH A CLEAVER BROOKS MODEL CB NTI-9 PPM ULTRA LOW NOX BURNER
	 
	3/28/2007
	9
	6.7

	33.6 MMBTU/HR SUPERIOR MODEL #8-5-400-S150-G-IC NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #NTD336NGXF9R ULTRA LOW NOX BURNER
	 
	4/16/2007
	9
	5.9

	8.4 MMBTU/HR DIXON MODEL SK-10 NATURAL GAS-FIRED BOILER WITH A MICRON FIBER-TECH MODEL MFT11X30 ULTRA LOW NOX BURNER
	 
	4/17/2007
	9
	4.9

	33.6 MMBTU/HR CLEAVER BROOKS MODEL #CBL700800150 NATURAL GAS-FIRED BOILER WITH AN ACT GIDEON RETRO MODEL #MGA-35 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	4/25/2007
	9
	7.3

	178 MMBTU/HR ZURN MODEL 22M KEYSTONE AUXILIARY BOILER WITH A TODD MODEL RMB ULTRA LOW NOX BURNER
	 
	5/2/2007
	9
	7.5

	10.5 MMBTU/HR NATURAL GAS-FIRED HURST S5X-250-150 BOILER WITH POWER FLAME NVC6-G-30 BURNER AND FLUE GAS RECIRCULATION
	 
	5/6/2007
	9
	8

	48.58 MMBTU/HR HURST MODEL S4-X-1200-150 NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOK MODEL NTS 504 NGX-FGR ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	5/8/2007
	9
	6.3

	14.65 MMBTU/HR CLEAVER-BROOKS MODEL CEW (LE9) 700-350-150ST NATURAL GAS-FIRED BOILER, WITH A CLEAVER-BROOKS MODEL LTD-147NGX-F9R ULTRA-LOW NOX BURNER
	 
	5/14/2007
	9
	8.8

	60.0 MMBTU/HR MURRAY IRON WORKS MODEL MG4E-25 NATURAL GAS-FIRED BOILER, WITH ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-60 9 PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	5/15/2007
	9
	7.7

	72.0 MMBTU/HR BABCOCK & WILCOX MODEL FM-1936 NATURAL GAS- FIRED BOILER, WITH ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-60 9 PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	5/15/2007
	9
	7.1

	26.0 MMBTU/HR BABCOCK & WILCOX NATURAL GAS-FIRED BOILER WITH AN ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-24 9 PPM ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	5/16/2007
	9
	6.4

	26.0 MMBTU/HR BABCOCK & WILCOX NATURAL GAS-FIRED BOILER WITH AN ADVANCED COMBUSTION TECHNOLOGY MODEL GIDION MGW-24 9 PPM ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	5/16/2007
	9
	7.9

	MODIFICATION OF THE 42 MMBTU/HR CLEAVER BROOKS MODEL D60-LH, NATURAL GAS-FIRED BOILER (#4), WITH AN ALZETA MODEL CSB420 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION TO LIMIT NOX EMISSIONS TO 7 PPMV @ 3% O2 FOR COMPLIANCE WITH RULE 4320.
	 
	5/23/2007
	9
	6.4

	32.66 MMBTU/HR CLEAVER-BROOKS (BOILER #2) MODEL CB200-800, 150# NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9PPM ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	5/29/2007
	9
	6.8

	25.1 MMBTU/HR CLEAVER-BROOKS MODEL CBLE 700-600-150 BOILER WITH A NATCOM ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION.
	 
	6/4/2007
	9
	6.2

	73.0 MMBTU/HR NEBRASKA BOILER MODEL NSE-58 NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB770R-LEA ULTRA LOW NOX BURNER.
	 
	6/19/2007
	9
	4.7

	32.66 MMBTU/HR CLEAVER-BROOKS MODEL CB200-800, 150# NATURAL GAS-FIRED BOILER #3 WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9 PPM ULTRA-LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM.
	 
	6/29/2007
	9
	6.5

	85 MMBTU/HR THERMOTICS NATURAL GAS/TEOR GAS-FIRED STEAM GENERATOR WITH NORTH AMERICAN MAGNAFLAME LOW-NOX BURNER, FGR, AND O2 CONTROLLER
	 
	7/9/2007
	9
	8.7

	130 MMBTU/HR NEBRASKA MODEL NSF-81 NATURAL GAS-FIRED BOILER WITH A TODD/RADIAN MODEL D-RMB128 BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	7/10/2007
	9
	6

	20.9 MMBTU/HR  CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER
	 
	7/12/2007
	9
	7.5

	20.9 MMBTU/HR CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	7/12/2007
	9
	7.2

	29.4 MMBTU/HR SUPERIOR, MODEL 4-5-3502, NATURAL GAS-FIRED BOILER WITH A POWER FLAME, MODEL NVC-12, ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	7/13/2007
	9
	5.4

	NEBRASKA MODEL NS-F-81 NATURAL GAS OR LPG-FIRED BOILER (WEST) WITH A 97 MMBTU/HR ALZETA MODEL CSB-1210 ULTRA-LOW NOX BURNER
	 
	7/13/2007
	9
	2.3

	NEBRASKA MODEL NS-F-81 NATURAL GAS OR LPG-FIRED BOILER (EAST) WITH A 97 MMBTU/HR ALZETA MODEL CSB-1210 ULTRA-LOW NOX BURNER 
	 
	7/13/2007
	9
	2.4

	31.5 MMBTU/HR HURST MODEL S5-X-750-200 NATURAL GAS-FIRED BOILER WITH A POWER FLAME MODEL LN1 NVC-13-G-30 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	7/20/2007
	9
	3.8

	21.966 MMBTU/HR WICKES NATURAL GAS-FIRED BOILER WITH A INDUSTRIAL COMBUSTION/NATCOM MODEL PF NTD 252GX9S-8 ULTRA-LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	7/20/2007
	9
	8.1

	26.4 MMBTU/HR HURST MODEL S400-700-150 NATURAL GAS-FIRED BOILER WITH A POWER FLAME MODEL NOVA PLUS-NVC12-G-30 ULTRA LOW NOX BURNER WITH INDUCED FGR
	 
	7/24/2007
	9
	5.6

	61.0 MMBTU/HR CLEAVER BROOKS BOILER EQUIPPED WITH NATURAL GAS OR PROPANE-AIRMIX-FIRED NATCOM HYPER-MIX MODEL P-61-G-26-1519 ULTRA LOW-NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	7/24/2007
	9
	7.1

	67.0 MMBTU/HR CLEAVER BROOKS MODEL DL-60 NATURAL GAS-FIRED BOILER WITH PROPANE AS SUPPLEMENTAL OR BACK-UP FUEL WITH TODD DRMB ULTRA LOW-NOX BURNER AND INDUCED FLUE GAS RECIRCULATION WITH O2 CONTROLLER
	 
	7/24/2007
	9
	7.3

	43 MMBTU/HR CLEAVER BROOKS MODEL #D-60E (#1) NATURAL GAS-FIRED BOILER WITH FUEL OIL #2 AS BACK-UP FUEL, A CLEAVER BROOKS MODEL NTS420LGS-09S-1P LOW NOX BURNER, AND FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	7/27/2007
	9
	5.1

	30 MMBTU/HR CLEAVER BROOKS MODEL D-24E (#2) NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD336NGX-F09R LOW NOX BURNER, A FLUE GAS RECIRCULATION (FGR) SYSTEM, AND FUEL OIL #2 AS BACK-UP FUEL
	 
	7/27/2007
	9
	5.8

	87 MMBTU/HR ERIE CITY IRON WORKS MODEL 1973 KEYSTONE NATURAL GAS-FIRED BOILER SERVED BY A NATCOM MODEL B-87-G-33-1824 BURNER AND INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM (BOILER #5)
	 
	7/30/2007
	9
	7.7

	85 MMBTU/HR PCL IDENTIFICATION #POSO-J402 NATURAL GAS-FIRED STEAM GENERATOR WITH A NORTH AMERICAN MODEL LE LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR), AND O2 CONTROLLER
	 
	8/1/2007
	9
	8

	NEBRASKA MODEL #NS-E-65 BOILER (#6) SERVED BY A 94 MMBTU/HR TODD/RADIAN MODEL RMB ULTRA LOW-NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	8/2/2007
	9
	8.2

	120.183 MMBTU/HR CLEAVER BROOKS BOILER, MODEL DLDH-102-E, WITH A TODD MODEL D-RMB ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM.  
	 
	8/6/2007
	9
	6.3

	29.92 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS, MODEL CB-700-700-200, BOILER (NO.2) WITH A CLEAVER BROOKS MODEL NTI-700 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	8/7/2007
	9
	6.4

	180 MMBTU/HR NEBRASKA BOILER, MODEL NO. N2S-7-95, WITH AN ULTRA LOW NOX TODD RAPID MIX BURNER (RMB) AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM WITH A ROSEMOUNT OXYGEN CONTROLLER.
	 
	8/8/2007
	9
	6.5

	36 MMBTU/HR NEBRASKA MODEL NS-C-S-42, NATURAL GAS-FIRED BOILER SERVED BY AN URS MODEL MRMB-4-36 ULTRA LOW NOX BURNER WITH AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM AND ROSEMOUNT O2 CONTROLLER
	 
	8/8/2007
	9
	7.3

	260 MMBTU/HR NEBRASKA MODEL #N2S-8/S-100-ECON NATURAL GAS FIRED BOILER WITH A TODD MODEL #D-RBM ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION.
	 
	8/8/2007
	9
	7

	25.1 MMBTU/HR CLEAVER BROOKS MODEL CB200-600, 150# PACKAGED FIRE-TUBE NATURAL GAS-FIRED BOILER, WITH ALZETA CSB-252R LOW-NOX BURNERS, AND O2 CONTROLLER
	 
	8/9/2007
	9
	6.7

	12.5 MMBTU/HR CLEAVER BROOKS MODEL #CBLE200-300 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CB(LE15) 700-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	8/9/2007
	9
	6.6

	12.5 MMBTU/HR CLEAVER BROOKS MODEL #CBLE200-300 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CB(LE15) 700-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	8/9/2007
	9
	6.6

	180.06 MMBTU/HR CLEAVER BROOKS MODEL DFE-E NATURAL GAS-FIRED BOILER WITH TODD DRMB ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	8/14/2007
	9
	8.2

	91 MMBTU/HR CLEAVER BROOKS MODEL DL-94 NATURAL GAS-FIRED BOILER WITH A NATCOM LOW NOX BURNER AND VFD CONTROLLED INDUCED FGR
	 
	8/14/2007
	9
	5.8

	34.6 MMBTU/HR ERIE CITY IRON WORKS MODEL TYPE VC BOILER #1 WITH A COEN MODEL ULN ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION.
	 
	8/20/2007
	9
	6.7

	21.0 MMBTU/HR SUPERIOR MODEL X6X2500S150-M SEMINOLE NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECHNOLOGY INC MODEL ACT 07-SLE ULTRA LOW NOX BURNER
	 
	9/10/2007
	9
	7.13

	NEBRASKA MODEL NS-F-81 NATURAL GAS OR LPG-FIRED BOILER (WEST) WITH A 97 MMBTU/HR ALZETA MODEL CSB-1210 ULTRA-LOW NOX BURNER
	 
	9/17/2007
	9
	1.9

	NEBRASKA MODEL NS-F-81 NATURAL GAS OR LPG-FIRED BOILER (EAST) WITH A 97 MMBTU/HR ALZETA MODEL CSB-1210 ULTRA-LOW NOX BURNER 
	 
	9/17/2007
	9
	2.2

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	9/24/2007
	9
	4.6

	31.5 MMBTU/HR JOHNSTON MODEL PFTA750-4G150S NATURAL GAS-FIRED BOILER WITH AN ACT GIDEON MODEL MGW-35 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR) 
	 
	9/28/2007
	9
	8

	25.1 MMBTU/HR CLEAVER BROOKS MODEL CB200-600, 150# PACKAGED FIRE-TUBE NATURAL GAS-FIRED BOILER, WITH ALZETA CSB-252R LOW-NOX BURNERS AND O2 CONTROLLER
	 
	10/26/2007
	9
	7

	32.0 MMBTU/HR CLEAVER BROOKS MODEL CB200-800-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL CB (LE9) 700-800 ULTRA LOW NOX BURNER AND INTERNAL BAFFLING FLUE GAS RECIRCULATION SYSTEM - BOILER #2
	 
	10/29/2007
	9
	5.1

	19.95 MMBTU/HR HURST MODEL S5X-500-150 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL NVC10-G-30 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	10/30/2007
	9
	5.8

	11.0 MMBTU/HR TEJAS, TRIPLE S MODEL NATURAL GAS-FIRED BOILER, WITH AN INDUSTRIAL COMBUSTION MODEL NTH110NG-09S-4P ULTRA LOW NOX BURNER, AND INDUCED FGR
	 
	11/1/2007
	9
	7

	178 MMBTU/HR ZURN MODEL 22M KEYSTONE AUXILIARY BOILER WITH A TODD MODEL RMB ULTRA LOW NOX BURNER
	 
	11/15/2007
	9
	6.3

	33.48 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS MODEL CB700-800-150ST BOILER WITH CB(LE9) 700-800 ULTRA LOW NOX BURNER - BOILER #1 
	 
	12/3/2007
	9
	6.7

	37.4 MMBTU/HR NATURAL GAS-FIRED BOILER WITH ALZETA LOW NOX BURNER
	 
	12/4/2007
	9
	5

	50.0 MMBTU/HR NEBRASKA BOILER MODEL #NS-D-49 WITH A NATCOM MODEL ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	12/12/2007
	9
	6.9

	25.1 MMBTU/HR IRON FIREMAN MODEL 30ZA-H-600 BOILER WITH A POWER FLAME MODEL NVC11 ULTRA LOW NOX BURNER (BOILER #3).
	 
	12/14/2007
	9
	6

	42.0 MMBTU/HR CLEAVER BROOKS MODEL CBL700-1000-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTS420NGX-09S-1P ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION AND AN O2 CONTROLLER
	 
	12/19/2007
	9
	6.6

	20.9 MMBTU/HR CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	12/20/2007
	9
	6.6

	20.9 MMBTU/HR  CLEAVER BROOKS MODEL #CB-200-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CBNTI-500-9PPM ULTRA LOW NOX BURNER
	 
	12/20/2007
	9
	8.1

	20.5 MMBTU/HR CLEAVER BROOKS MODEL CBLE-NIT-500-200ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS NTI MODEL CBLE-700-500-200ST ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	12/28/2007
	9
	6.8

	20.925 MMBTU/HR HURST, MODEL S4 GP2 500 200 BOILER WITH A POWER FLAME NOVA PLUS BURNER, MODEL LN1NVC10-G-30 ULTRA LOW-NOX BURNER.
	 
	1/4/2008
	9
	7.2

	16.73 MMBTU/HR CLAYTON INDUSTRIES, MODEL EG404-2-FMB, STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL UH-30672 LOW NOX BURNER
	 
	1/14/2008
	9
	11.8

	16.73 MMBTU/HR CLAYTON INDUSTRIES, MODEL EG404-2-FMB, STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL UH-30672 LOW NOX BURNER
	 
	1/14/2008
	9
	7.9

	21.0 MMBTU/HR HURST MODEL S5-X-500-150 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL NVC-10-G-30 ULTRA-LOW NOX BURNER
	 
	1/15/2008
	9
	6.9

	75.6 MMBTU/HR SUPERIOR MODEL SEMINOLE 3 PASS, OR EQUIVALENT, NATURAL GAS-FIRED BOILER #1 WITH AN ALZETA MODEL CSB 756, OR EQUIVALENT, ULTRA LOW-NOX BURNER, AND FORCED FLUE GAS RECIRCULATION
	 
	1/15/2008
	9
	5.6

	75.6 MMBTU/HR SUPERIOR MODEL SEMINOLE 3 PASS, OR EQUIVALENT, NATURAL GAS-FIRED BOILER #2 WITH AN ALZETA MODEL CSB 756, OR EQUIVALENT, ULTRA LOW-NOX BURNER, AND FORCED FLUE GAS RECIRCULATION
	 
	1/15/2008
	9
	6.3

	16.8 MMBTU/HR HURST BOILER WITH A POWERFLAME ULTRA LOW NOX BURNER
	 
	1/16/2008
	9
	4.6

	12.6 MMBTU/HR NATURAL GAS FIRED WHIRLPOWER SPACE CONDITIONER BOILER WITH A POWERFLAME MODEL NVC-7-G-30 ULTRA-LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	1/17/2008
	9
	5.3

	5.05 MMBTU/HR CLAYTON MODEL SFG-125-SE-FMB NATURAL GAS-FIRED BOILER WITH A CLAYTON MODEL 125FMB ULTRA LOW NOX BURNER
	 
	1/23/2008
	9
	3

	19.950 MMBTU/HR HURST MODEL #S 2500-150-86 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL #NVC-10-G-30 ULTRA LOW-NOX BURNER
	 
	2/12/2008
	9
	6.3

	16.8 MMBTU HURST MODEL S5-X-400-150 NATURAL GAS-FIRED BOILER WITH POWER FLAME MODEL NVC9-G-30 ULTRA LOW NOX BURNER
	 
	2/13/2008
	9
	3.8

	20.9 MMBTU/HR CLEAVER BROOKS MODEL FIRETUBE 4WG700-500 200 BOILER WITH INDUSTRIAL COMBUSTION MODEL PROFIRE ULTRA LOW NOX BURNER INCLUDING FLUE GAS RECIRCULATION SYSTEM AND O2 CONTROLLER.
	 
	3/11/2008
	9
	4.8

	32.66 MMBTU/HR CLEAVER-BROOKS MODEL CB200-800, 150# NATURAL GAS-FIRED BOILER #3 WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9 PPM ULTRA-LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM.
	 
	3/13/2008
	9
	5.2

	33.0 MMBTU/HR CLEAVER-BROOKS (BOILER #1) MODEL CB 200-800 WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9PPM ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	3/13/2008
	9
	6.7

	29.4 MMBTU/HR HURST MODEL 400 G/P 700-150 NATURAL GAS-FIRED BOILER, WITH PROPANE AS A BACK-UP FUEL, WITH A CLEAVER-BROOKS MODEL NTD294NGX-09S-8P ULTRA LOW NOX BURNER 
	 
	3/17/2008
	9
	7.4

	28.5 MMBTU/HR HURST MODEL 400 G/P 700-150 NATURAL GAS-FIRED BOILER  SERVED BY A CLEAVER BROOKS MODEL NTD294NGX-095-8P ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR) SYSTEM WITH PROPANE AS BACKUP FUEL
	 
	3/17/2008
	9
	7.6

	10.5 MMBTU/HR NATURAL GAS-FIRED HURST S5X-250-150 BOILER WITH POWER FLAME NVC6-G-30 BURNER AND FLUE GAS RECIRCULATION
	 
	3/19/2008
	9
	7.4

	28.6 MMBTU/HR CLEAVER-BROOKS MODEL CB-700 SYSTEM 20 NATURAL GAS/PROPANE-FIRED BOILER WITH A CLEAVER-BROOKS MODEL NTI-15-700 ULTRA LOW NOX BURNER, FGR, AND O2 TRIM SYSTEM
	 
	3/25/2008
	9
	6.1

	21.0 MMBTU/HR NATURAL GAS-FIRED PACKAGE BOILER WITH A JOHN ZINK ULTRA LOW NOX BURNER AND FGR
	 
	4/4/2008
	9
	6.2

	ONE 34.6 MMBTU/HR ERIE CITY IRON WORKS MODEL TYPE VC BOILER #2 WITH A COEN MODEL ULN ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	4/9/2008
	9
	8.3

	85 MMBTU/HR PCL IDENTIFICATION #POSO-J404 NATURAL/TEOR GAS-FIRED STEAM GENERATOR WITH A NORTH AMERICAN MAGNA-FLAME LE LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR), AND O2 CONTROLLER
	 
	4/11/2008
	9
	8.5

	6.3 MMBTU/HR CLAYTON INDUSTRIES MODEL SEG-154-FMB NATURAL GAS-FIRED STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL 154FMB ULTRA LOW-NOX BURNER
	 
	4/17/2008
	9
	4.5

	33.6 MMBTU/HR CLEAVER BROOKS MODEL #CBL700800150 NATURAL GAS-FIRED BOILER WITH AN ACT GIDEON RETRO MODEL #MGA-35 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	5/1/2008
	9
	8

	19.95 MMBTU/HR NATURAL GAS FIRED HURST MODEL S5X-500-150 BOILER EQUIPPED WITH A POWERFLAME MODEL NVC10-G-30 BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	5/13/2008
	9
	4.3

	19.95 MMBTU/HR HURST MODEL S5X-500-150 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL NVC10-G-30 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	5/13/2008
	9
	4.2

	12.5 MMBTU/HR CLEAVER BROOKS MODEL #CBLE200-300 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CB(LE15) 700-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	5/20/2008
	9
	7.3

	MODIFICATION OF THE 42 MMBTU/HR CLEAVER BROOKS MODEL D60-LH, NATURAL GAS-FIRED BOILER (#4), WITH AN ALZETA MODEL CSB420 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION TO LIMIT NOX EMISSIONS TO 7 PPMV @ 3% O2 FOR COMPLIANCE WITH RULE 4320.
	 
	5/29/2008
	9
	6

	16.75 MMBTU/HR CLEAVER-BROOKS MODEL CBI 200-400-150 BOILER WITH CLEAVER-BROOKS MODEL NTI-400 LOW-NOX BURNER
	 
	5/30/2008
	9
	7.9

	25.1 MMBTU/HR JOHNSON MODEL 534-CG BOILER SERVED BY A POWER FLAME MODEL NCV11 ULTRA LOW NOX BURNER (BOILER #1).
	 
	6/3/2008
	9
	4.5

	25.1 MMBTU/HR JOHNSON MODEL 534-CG BOILER SERVED BY A POWER FLAME MODEL NBVC11 ULTRA LOW NOX BURNER (BOILER #2).
	 
	6/3/2008
	9
	5.6

	25.1 MMBTU/HR HURST MODEL S4-G-600-150 BOILER SERVED BY A POWER FLAME MODEL NVC117 ULTRA LOW NOX BURNER.
	 
	6/3/2008
	9
	6.9

	180 MMBTU/HR NEBRASKA BOILER, MODEL NO. N2S-7-95, WITH AN ULTRA LOW NOX TODD RAPID MIX BURNER (RMB) AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM WITH A ROSEMOUNT OXYGEN CONTROLLER.
	 
	6/9/2008
	9
	6.4

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	6/10/2008
	9
	6.5

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	6/10/2008
	9
	6.5

	260 MMBTU/HR NEBRASKA MODEL #N2S-8/S-100-ECON NATURAL GAS FIRED BOILER WITH A TODD MODEL #D-RBM ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION.
	 
	6/19/2008
	9
	7.5

	34.6 MMBTU/HR ERIE CITY IRON WORKS MODEL TYPE VC BOILER #3 WITH A COEN MODEL QLA 20.0 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	6/20/2008
	9
	7.5

	25.1 MMBTU/HR CLEAVER-BROOKS MODEL CBLE 700-600-150 BOILER WITH A NATCOM ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION.
	 
	6/25/2008
	9
	6.8

	120.183 MMBTU/HR CLEAVER BROOKS BOILER, MODEL DLDH-102-E, WITH A TODD MODEL D-RMB ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM.  
	 
	6/26/2008
	9
	6.2

	120.183 MMBTU/HR CLEAVER BROOKS BOILER, MODEL DLDH-102-E, WITH A TODD MODEL D-RMB ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM.  
	 
	7/1/2008
	9
	6.9

	85 MMBTU/HR THERMOTICS NATURAL GAS/TEOR GAS-FIRED STEAM GENERATOR WITH NORTH AMERICAN MAGNAFLAME LOW-NOX BURNER, FGR, AND O2 CONTROLLER
	 
	7/9/2008
	9
	7.8

	120 MMBTU/HR NEBRASKA MODEL #NS-F-81-ECON NATURAL GAS-FIRED BOILER WITH A TODD/RADIAN CORPORATION MODEL #D-RMB ULTRA LOW NOX BURNER WITH INDUCED FLUE GAS RECIRCULATION (FGR)
	 
	7/14/2008
	9
	6.5

	36 MMBTU/HR NEBRASKA MODEL NS-C-S-42, NATURAL GAS-FIRED BOILER SERVED BY AN URS MODEL MRMB-4-36 ULTRA LOW NOX BURNER WITH AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM AND ROSEMOUNT O2 CONTROLLER
	 
	7/15/2008
	9
	6.9

	260 MMBTU/HR NEBRASKA MODEL #N2S-8/S-100-ECON NATURAL GAS FIRED BOILER WITH A TODD MODEL #D-RBM ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION.
	 
	7/16/2008
	9
	5.6

	16.8 MMBTU/HR SUPERIOR MOHAWK 4--2007-S150-GP-G NATURAL GAS FIRED BOILER WITH FGR RECIRCULATION AND GORDON-PIATT ULTRA LOW NOX BURNER
	 
	7/16/2008
	9
	8.3

	95 MMBTU/HR CLEAVER BROOKS MODEL #DL94E NATURAL GAS-FIRED BOILER (#2) WITH TODD RMB ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION SYSTEM, AND OXYGEN CONTROLLER
	 
	7/21/2008
	9
	7.2

	42 MMBTU/HR HURST MODEL SERIES 500 NATURAL GAS-FIRED BOILER WITH AN ADVANCE COMBUSTION TECH MODEL MGA 42 LONOX ULTRA LOW NOX BURNER
	 
	7/23/2008
	9
	8.3

	99.9 MMBTU/HR CLEAVER BROOKS MODEL #DL-94RH PACKAGED WATERTUBE STEAM BOILER #2 WITH TODD MODEL C-RMB ULTRA LOW NOX BURNER, KENETUBE FINNED TUBE ECONOMIZER, OXYGEN TRIM SYSTEM, AND INDUCED FGR
	 
	7/29/2008
	6
	5.6

	99.9 MMBTU/HR CLEAVER BROOKS MODEL #DL-94RH PACKAGED WATERTUBE STEAM BOILER #1 WITH TODD MODEL C-RMB ULTRA LOW NOX BURNER, KENETUBE FINNED TUBE ECONOMIZER, OXYGEN TRIM SYSTEM, AND INDUCED FGR
	 
	7/29/2008
	6
	5.1

	14.2 MMBTU/HR CLEAVER BROOKS MODEL CBI700-350-150 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTI700-350 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	8/6/2008
	9
	7.8

	63.0 MMBTU/HR CLEAVER BROOKS, MODEL CBL-700-1500, NATURAL GAS-FIRED BOILER WITH AN INDUSTRIAL COMBUSTION, MODEL NTS2-630, ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	8/7/2008
	9
	6.3

	31.5 MMBTU/HR HURST MODEL S5-X-750-200 NATURAL GAS-FIRED BOILER WITH A POWER FLAME MODEL LN1 NVC-13-G-30 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	8/8/2008
	9
	3.8

	120 MMBTU/HR NEBRASKA MODEL NOS-2A-67 NATURAL GAS-FIRED BOILER WITH NATCOM BURNER MODEL P-120-LOG-31-1723 AND FLUE GAS RECIRCULATION SYSTEM
	 
	8/12/2008
	9
	8.7

	184 MMBTU/HR BABCOCK & WILCOX MODEL FM117-97 NATURAL GAS-FIRED BOILER WITH A TODD RAPID MIX ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	8/15/2008
	9
	7.5

	181.0 MMBTU/HR NEBRASKA MODEL N2S-7-89 BOILER #6 EQUIPPED WITH A NATCOM MODEL P-182-G-44-2035 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	8/26/2008
	9
	7.5

	14.7 MMBTU/HR HURST MODEL SE-X-350-150 NATURAL GAS-FIRED BOILER WITH A POWER FLAME MODEL NVC9-G-30 ULTRA LOW NOX BURNER
	 
	9/2/2008
	9
	5.3

	33.6 MMBTU/HR CLEAVER BROOKS BOILER (#1) WITH POWER FLAME MODEL NVC12CBR-G-30 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	9/3/2008
	9
	7.1

	33.6 MMBTU/HR CLEAVER BROOKS BOILER (#2) WITH POWER FLAME MODEL NVC12CBR-G-30 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	9/8/2008
	9
	5.1

	34.6 MMBTU/HR ERIE CITY IRON WORKS MODEL TYPE VC BOILER #1 WITH A COEN MODEL ULN ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION.
	 
	9/19/2008
	9
	8

	33.6 MMBTU/HR SUPERIOR BOILER MODEL # 6X4000200ACT NATURAL GAS-FIRED AMERICAN COMBUSTION TECHNOLOGY BOILER WITH POWER FLAME MODEL #NVC13-G-30 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	10/2/2008
	9
	6.3

	20.5 MMBTU/HR CLEAVER BROOKS MODEL CBLE-NIT-500-200ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS NTI MODEL CBLE-700-500-200ST ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	10/23/2008
	9
	8.7

	43.4 MMBTU/HR  NEBRASKA MODEL NS-C-42-ECON NATURAL GAS-FIRED BOILER, EQUIPPED WITH AN ALZETA ULTRA-LOW NOX BURNER WITH A VARIABLE FREQUENCY DRIVE FOR AIR INTAKE FAN MOTOR AND OXYGEN TRIM EQUIPMENT IN EXHAUST STACK
	 
	11/4/2008
	9
	5.8

	20.9 MMBTU/HR SUPERIOR MODEL 6-5-2500 BOILER SERVED BY AN AMERICAN COMBUSTION TECHNOLOGY, INC. MODEL SLE-07 ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM 
	 
	11/7/2008
	9
	7.5

	31.5 MMBTU/HR JOHNSTON MODEL PFTA750-4G150S NATURAL GAS-FIRED BOILER WITH AN ACT GIDEON MODEL MGW-35 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR) 
	 
	11/12/2008
	9
	7.9

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER AND FGR, APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	11/12/2008
	9
	7

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER AND FGR, APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	11/12/2008
	9
	6

	63 MMBTU/HR HURST SERIES 400 FIRETUBE NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB630 ULTRA LOW NOX BURNER
	 
	11/25/2008
	9
	4.1

	60.6 MMBTU/HR NEBRASKA MODEL NS-C-61-ECON NATURAL GAS FIRED BOILER WITH AN ALZETA MODEL CSB642R-LEA ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	11/26/2008
	9
	7.5

	19.0 MMBTU/HR NATURAL GAS/PROPANE-FIRED STEAM GENERATOR WITH GIDEON ULTRA LOW NOX BURNER MODEL MGW-25R1 OR EQUIVALENT
	 
	12/2/2008
	9
	8.4

	16.8 MMBTU/HR HURST BOILER WITH A POWERFLAME ULTRA LOW NOX BURNER
	 
	12/12/2008
	9
	7.4

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #2)
	 
	12/16/2008
	9
	5.8

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #1)
	 
	12/17/2008
	9
	5.79

	25.1 MMBTU/HR IRON FIREMAN MODEL 30ZA-H-600 BOILER WITH A POWER FLAME MODEL NVC11 ULTRA LOW NOX BURNER (BOILER #3).
	 
	12/17/2008
	9
	6.7

	20.925 MMBTU/HR HURST, MODEL S4 GP2 500 200 BOILER WITH A POWER FLAME NOVA PLUS BURNER, MODEL LN1NVC10-G-30 ULTRA LOW-NOX BURNER.
	 
	1/6/2009
	9
	5.0

	21.0 MMBTU/HR HURST MODEL S5-X-500-150 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL NVC-10-G-30 ULTRA-LOW NOX BURNER
	 
	1/6/2009
	9
	6.7

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #3)
	 
	1/7/2009
	9
	6.5

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #4)
	 
	1/7/2009
	9
	6.5

	42.0 MMBTU/HR CLEAVER BROOKS MODEL CBL700-1000-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTS420NGX-09S-1P ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION AND AN O2 CONTROLLER
	 
	1/12/2009
	9
	7.9

	16.73 MMBTU/HR CLAYTON INDUSTRIES, MODEL EG404-2-FMB, STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL UH-30672 LOW NOX BURNER
	 
	1/13/2009
	9
	5.0

	16.73 MMBTU/HR CLAYTON INDUSTRIES, MODEL EG404-2-FMB, STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL UH-30672 LOW NOX BURNER
	 
	1/13/2009
	9
	5.02

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #5)
	 
	1/16/2009
	9
	6.3

	8.4 MMBTU/HR CLAYTON INDUSTRIES MODEL SFG-200-M-FMB-1 NATURAL GAS-FIRED STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL 200 FMB ULTRA LOW NOX BURNER
	 
	1/16/2009
	9
	6.5

	14.7 MMBTU/HR CLAYTON INDUSTRIES MODEL SEG-354-FMB-2 BOILER SERVED BY A CLAYTON INDUSTRIES MODEL SEG-354-FMB ULTRA LOW NOX BURNER
	 
	1/21/2009
	9
	7.4

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER AND FGR, APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	2/5/2009
	9
	7

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER AND FGR, APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	2/5/2009
	9
	7

	5.05 MMBTU/HR CLAYTON MODEL SFG-125-SE-FMB NATURAL GAS-FIRED BOILER WITH A CLAYTON MODEL 125FMB ULTRA LOW NOX BURNER
	 
	2/11/2009
	9
	7

	19.950 MMBTU/HR HURST MODEL #S 2500-150-86 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL #NVC-10-G-30 ULTRA LOW-NOX BURNER
	 
	2/24/2009
	9
	4.5

	12.5 MMBTU/HR CLEAVER BROOKS MODEL #CBLE200-300 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL #CB(LE15) 700-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	2/24/2009
	9
	7.2

	6.3 MMBTU/HR CLAYTON INDUSTRIES MODEL SFG-150M-1 NATURAL GAS-FIRED STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL 150 FMB ULTRA LOW NOX BURNER
	 
	2/25/2009
	9
	6.3

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #6)
	 
	2/27/2009
	9
	6.7

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #7)
	 
	2/27/2009
	9
	6.5

	33.6 MMBTU/HR SUPERIOR MODEL 8-5-400-S150-G-IC NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD336NGX ULTRA LOW NOX BURNER
	 
	2/27/2009
	9
	6.6

	16.8 MMBTU HURST MODEL S5-X-400-150 NATURAL GAS-FIRED BOILER WITH POWER FLAME MODEL NVC9-G-30 ULTRA LOW NOX BURNER
	 
	3/10/2009
	9
	4.1

	24 MMBTU/HR NATURAL GAS-FIRED MURRAY IRONWORKS MODEL MCF2-50 BOILER WITH GORDON PIATT MODEL FRMB17-500 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	3/11/2009
	9
	7.8

	33.0 MMBTU/HR CLEAVER-BROOKS (BOILER #1) MODEL CB 200-800 WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9PPM ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	3/11/2009
	9
	7.9

	63 MMBTU/HR HURST SERIES 400 NATURAL GAS FIRED BOILER WITH AN NOVA PLUS ULTRA LOW NOX COMBUSTION SYSTEM MODEL NVC17-G-40 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	3/17/2009
	8.3
	3.9

	63 MMBTU/HR HURST SERIES 400 NATURAL GAS FIRED BOILER WITH AN NOVA PLUS ULTRA LOW NOX COMBUSTION SYSTEM MODEL NVC17-G-40 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	3/17/2009
	8.3
	3.2

	99 MMBTU/HR UNION IRON WORKS MODEL MH NATURAL GAS/PROPANE-FIRED FORCED DRAFT BOILER WITH VARIABLE FREQUENCY DRIVE BLOWER AND TODD RAPID MIX BURNER
	 
	3/17/2009
	9
	5.5

	20.9 MMBTU/HR CLEAVER BROOKS MODEL 700-500 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL PROFIRE NT ULTRA LOW NOX BURNER
	 
	3/18/2009
	9
	6.8

	5.0 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS MODEL FLX200-550-160HW BOILER WITH AN INDUSTRIAL COMBUSTION MODEL NTH55LG-A-15S ULTRA LOW-NOX BURNER
	 
	3/31/2009
	9
	9

	6.3 MMBTU/HR CLAYTON INDUSTRIES MODEL SEG-154-FMB NATURAL GAS-FIRED STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL 154FMB ULTRA LOW-NOX BURNER
	 
	4/17/2009
	9
	6.8

	85 MMBTU/HR PCL IDENTIFICATION #POSO-J404 NATURAL/TEOR GAS-FIRED STEAM GENERATOR WITH A NORTH AMERICAN MAGNA-FLAME LE LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR), AND O2 CONTROLLER
	 
	4/20/2009
	9
	7.8

	32.7 MMBTU/HR CLEAVER-BROOKS MODEL #CBLE700-800-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	4/23/2009
	9
	7.7

	21.0 MMBTU/HR NATURAL GAS-FIRED PACKAGE BOILER WITH A JOHN ZINK ULTRA LOW NOX BURNER AND FGR
	 
	4/29/2009
	9
	4.2

	48.58 MMBTU/HR HURST MODEL S4-X-1200-150 NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOK MODEL NTS 504 NGX-FGR ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	5/6/2009
	9
	8.0

	85 MMBTU/HR NATURAL GAS-FIRED STEAM GENERATOR #MNJ-406 WITH A NORTH AMERICAN MAGNA-FLAME LE BURNER, FLUE GAS RECIRCULATION, AND AN O2 CONTROLLER
	 
	5/7/2009
	9
	7.9

	21.0 MMBTU/HR BABCOCK & WILCOX MODEL FM TYPE D NATURAL GAS-FIRED BOILER WITH A POWERFLAME ULTRA LOW NOX NOVA PLUS MODEL NVC10-G-30 BURNER
	 
	5/12/2009
	9
	5.8

	24.494 MMBTU/HR CLEAVER BROOKS MODEL CBI 200-600,200 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTI-9 ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	5/12/2009
	9
	6.6

	12.6 MMBTU/HR CLEAVER BROOKS MODEL C-B-200-300 NATURAL GAS FIRED BOILER EQUIPPED WITH AN ALZETA MODEL CSB126R LOW NOX BURNER
	 
	5/19/2009
	9
	5

	16.75 MMBTU/HR CLEAVER-BROOKS MODEL CBI 200-400-150 BOILER WITH CLEAVER-BROOKS MODEL NTI-400 LOW-NOX BURNER
	 
	5/26/2009
	9
	7.4

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB200-500 NATURAL GAS-FIRED BOILER WITH FUEL OIL #2 AS A BACK-UP FUEL, AND EQUIPPED WITH CLEAVER BROOKS MODEL CBNT ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	5/27/2009
	9
	5.9

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CEW LN200-500,150# NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD2106 GA-FO9R ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	5/27/2009
	9
	8

	ONE 20.9 MMBTU/HR CLEAVER BROOKS MODEL CEW LN200-500,150# NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTD2106 GA-FO9R ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	5/27/2009
	9
	7.9

	42.25 MMBTU/HR CLEAVER BROOKS NATURAL GAS-FIRED BOILER (#3), OXYGEN TRIM, FLUE GAS RECIRCULATION, AND ALZETA MODEL CSB-420-LEA ULTRA LOW NOX BURNER 
	 
	5/28/2009
	9
	4.2

	8.4 MMBTU/HR PROPANE-FUELED HURST BOILER MODEL S5-X-200-150 PROPANE FUELED BOILER EQUIPPED WITH A POWER FLAME NOVA ULTRA LOW-NOX MODEL NVC6-G-30 BURNER
	 
	5/29/2009
	9
	8.6

	84 MMBTU/HR THERMOTICS NATURAL & TEOR GAS-FIRED STEAM GENERATOR W/ MAGNA FLAME MODEL 4231-85-GLE-X2631 BURNER, FGR, AND RADAC O2 CONTROLLER
	 
	6/1/2009
	9
	7.8

	184 MMBTU/HR BABCOCK & WILCOX MODEL FM117-97 NATURAL GAS-FIRED BOILER WITH A TODD RAPID MIX ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	6/9/2009
	9
	7.3

	19.95 MMBTU/HR HURST MODEL 54X-500-15 NATURAL GAS-FIRED BOILER WITH A POWERFLAME MODEL NVC-10-G-30 ULTRA-LOW NOX BURNER
	 
	6/10/2009
	9
	5.8

	20.925 MMBTU/HR CLEAVER BROOKS MODEL CBI 700 500 250 BOILER EQUIPPED WITH A CLEAVER BROOKS MODEL NTI-500-9 BURNER AND INDUCED FLUE GAS RECIRCULATION SYSTEM  
	 
	6/11/2009
	9
	6.4

	122 MMBTU/HR NATURAL GAS-FIRED BOILER WITH FLUE GAS RECIRCULATION, JOHN ZINK TODD RMB MODEL TI450IGO3650X LOW NOX BURNER AND OXYGEN CONTROLLER
	 
	6/11/2009
	9
	8.1

	25.1 MMBTU/HR BURNHAM MODEL #LN3P-600-50-G-BNHM NATURAL GAS-FIRED BOILER WITH A PROFIRE NT MODEL NTD 252 NG X-F9R ULTRA LOW NOX BURNER
	 
	6/26/2009
	9
	7.1

	33.48 MMBTU/HR CLEAVER BROOKS MODEL CB700-800-150ST NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL CB(LE9)700-800 BURNER WITH FLUE GAS RECIRCULATION
	 
	6/29/2009
	9
	7.6

	42 MMBTU/HR HURST MODEL SERIES 500 NATURAL GAS-FIRED BOILER WITH AN ADVANCE COMBUSTION TECH MODEL MGA 42 LONOX ULTRA LOW NOX BURNER
	 
	7/10/2009
	9
	8.5

	62.5 MMBTU/HR NATIONAL CO. NATURAL GAS/PROPANE/PRODUCTION GAS-FIRED STEAM GENERATOR WITH A MAGNA FLAME MODEL 4231 G-LE ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	7/13/2009
	7
	7

	130 MMBTU/HR NEBRASKA MODEL NSF-81 NATURAL GAS-FIRED BOILER WITH A TODD/RADIAN MODEL D-RMB128 BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	7/14/2009
	9
	6.5

	120 MMBTU/HR NEBRASKA MODEL #NS-F-81-ECON NATURAL GAS-FIRED BOILER WITH A TODD/RADIAN CORPORATION MODEL #D-RMB ULTRA LOW NOX BURNER WITH INDUCED FLUE GAS RECIRCULATION (FGR)
	 
	7/14/2009
	9
	7.2

	118.5 MMBTU/HR NEBRASKA MODEL #NS-F-81-ECON NATURAL GAS-FIRED BOILER WITH A TODD/RADIAN CORPORATION MODEL #D-RMB LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	7/14/2009
	9
	6.7

	205 MMBTU/HR NEBRASKA MODEL #N2S-7/S-95-ECON NATURAL GAS-FIRED BOILER WITH A TODD/RADIAN CORPORATION MODEL #D-RMB ULTRA LOW NOX BURNER
	 
	7/14/2009
	9
	7

	6.3 MMBTU/HR CLAYTON INDUSTRIES MODEL SFG-150M-FMB-SSE BOILER WITH A CLAYTON INDUSTRIES MODEL 150 FMB ULTRA LOW-NOX BURNER
	 
	7/14/2009
	9
	8.4

	91 MMBTU/HR NEBRASKA MODEL # NS-E-59 NATURAL GAS-FIRED BOILER WITH A TODD/RADIAN CORPORATION MODEL #D-RMB RAPID MIX ULTRA LOW NOX BURNER
	 
	7/15/2009
	9
	7.1

	111 MMBTU/HR BABCOCK & WILCOX MODEL FF-16 NATURAL GAS-FIRED BOILER (#3) WITH A TODD MODEL RADIAN LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	7/21/2009
	9
	6

	196 MMBTU/HR BABCOCK & WILCOX MODEL FF-16 NATURAL GAS-FIRED BOILER (#4) WITH A TODD MODEL RADIAN LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)
	 
	7/21/2009
	9
	6

	33.4 MMBTU/HR CLEAVER-BROOKS MODEL CBLE 700-800-250 NATURAL GAS-FIRED BOILER WITH LOW NOX BURNER
	 
	7/23/2009
	9
	8

	14.2 MMBTU/HR CLEAVER BROOKS MODEL CBI700-350-150 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTI700-350 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	7/24/2009
	9
	6.6

	34.6 MMBTU/HR ERIE CITY IRON WORKS MODEL TYPE VC BOILER #3 WITH A COEN MODEL QLA 20.0 ULTRA LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM
	 
	7/24/2009
	9
	8

	99.9 MMBTU/HR CLEAVER BROOKS MODEL #DL-94RH PACKAGED WATERTUBE STEAM BOILER #2 WITH TODD MODEL C-RMB ULTRA LOW NOX BURNER, KENETUBE FINNED TUBE ECONOMIZER, OXYGEN TRIM SYSTEM, AND INDUCED FGR
	 
	7/28/2009
	6
	4.8

	99.9 MMBTU/HR CLEAVER BROOKS MODEL #DL-94RH PACKAGED WATERTUBE STEAM BOILER #1 WITH TODD MODEL C-RMB ULTRA LOW NOX BURNER, KENETUBE FINNED TUBE ECONOMIZER, OXYGEN TRIM SYSTEM, AND INDUCED FGR
	 
	7/28/2009
	6
	4

	99.9 MMBTU/HR CLEAVER BROOKS MODEL DL-94RH PACKAGED WATERTUBE STEAM BOILER #3 WITH TODD MODEL C-RMB ULTRA LOW NOX BURNER, KENTUBE FINNED TUBE ECONOMIZER, OXYGEN TRIM SYSTEM, AND INDUCED FGR  
	 
	7/28/2009
	6
	4.7

	85 MMBTU/HR BABCOCK & WILCOX MODEL FMD-10 BOILER WITH NATCOM MODEL B-85-G-35-2126 LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM (BOILER #3)
	 
	7/28/2009
	9
	5.5

	180 MMBTU/HR NEBRASKA BOILER, MODEL NO. N2S-7-95, WITH AN ULTRA LOW NOX TODD RAPID MIX BURNER (RMB) AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM WITH A ROSEMOUNT OXYGEN CONTROLLER.
	 
	8/4/2009
	9
	7.3

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	8/4/2009
	9
	7.2

	260 MMBTU/HR NEBRASKA MODEL #N2S-8/S-100-ECON NATURAL GAS FIRED BOILER WITH A TODD MODEL #D-RBM ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION.
	 
	8/4/2009
	9
	6.4

	29.3 MMBTU/HR CLEAVER BROOKS BOILER MODEL #CB 400-700-150 WITH A CLEAVER BROOKS MODEL #CB-NTI-9PPM ULTRA LOW-NOX BURNER AND FLUE GAS RECIRCULATION
	 
	8/4/2009
	9
	5.2

	220 MMBTU/HR NATURAL GAS-FIRED NEBRASKA MODEL N-25-8/S-100-ECON BOILER WITH A TODD DRMB BURNER AND FLUE GAS RECIRCULATION
	 
	8/5/2009
	9
	7.3

	20.925 MMBTU/HR HURST MODEL S4-X-500-150# NATURAL GAS-FIRED BOILER WITH AN INDUSTRIAL COMBUSTION MODEL NTD210NGX-09S-6P ULTRA LOW NOX BURNER WITH FLUE GAS RECIRCULATION
	 
	8/11/2009
	9
	6.9

	MODIFICATION OF THE 42 MMBTU/HR CLEAVER BROOKS MODEL D60-LH, NATURAL GAS-FIRED BOILER (#4), WITH AN ALZETA MODEL CSB420 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION TO LIMIT NOX EMISSIONS TO 7 PPMV @ 3% O2 FOR COMPLIANCE WITH RULE 4320.
	 
	8/11/2009
	9
	6.3

	16.8 MMBTU/HR SUPERIOR MOHAWK 4--2007-S150-GP-G NATURAL GAS FIRED BOILER WITH FGR RECIRCULATION AND GORDON-PIATT ULTRA LOW NOX BURNER
	 
	8/11/2009
	9
	7.2

	29.4 MMBTU/HR CLEAVER BROOKS MODEL CBI 700 NATURAL GAS-FIRED BOILER WITH A ERIB GIDEON MODEL ERIB 800 ULTRA LOW NOX BURNER
	 
	8/13/2009
	9
	8.9

	20.9 MMBTU/HR CLEAVER-BROOKS MODEL CB 700-500,200# NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOKS MODEL NTI-500 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	8/19/2009
	9
	7.6

	21 MMBTU/HR IRON FIREMAN MODEL 300-777 BOILER WITH AN ALZETA MODEL CSB22-250-30/15 LOW-NOX BURNER
	 
	8/31/2009
	9
	5.5

	25.3 MMBTU/HR HURST, MODEL NO. SERIES 400, NATURAL GAS/PROPANE-FIRED BOILER WITH AN ALZETA MODEL CSB252-LEA BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	8/31/2009
	9
	5.8

	14.7 MMBTU/HR CLAYTON INDUSTRIES MODEL SEG-354-FMB-2 BOILER SERVED BY A CLAYTON INDUSTRIES MODEL SEG-354-FMB ULTRA LOW NOX BURNER
	 
	9/1/2009
	9
	8

	19.95 MMBTU/HR JOHNSTON MODEL PFTX-500-150S NATURAL GAS-FIRED BOILER WITH A GORDON PIATT MODEL RMB-G500 MARK ULTRA LOW NOX BURNER AND FGR
	 
	9/2/2009
	9
	7.6

	14.7 MMBTU/HR HURST MODEL SE-X-350-150 NATURAL GAS-FIRED BOILER WITH A POWER FLAME MODEL NVC9-G-30 ULTRA LOW NOX BURNER
	 
	9/3/2009
	9
	6.5

	120.183 MMBTU/HR CLEAVER BROOKS BOILER, MODEL DLDH-102-E, WITH A TODD MODEL D-RMB ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION SYSTEM.  
	 
	9/4/2009
	9
	8

	33.5 MMBTU/HR CLEAVER BROOKS MODEL #CB800 NATURAL GAS-FIRED FIRETUBE BOILER WITH AN ERI MODEL LNRETRO FORCED DRAFT ULTRA LOW-NOX BURNER WITH FLUE GAS RE-CIRCULATION (FGR) AND EQUIPPED WITH A NATURAL GAS FLOW METER
	 
	9/9/2009
	9
	5.5

	CLEAVER-BROOKS (MODEL CB-200-800-150) BOILER WITH ALZETA 24.5 MMBTU/HR LOW-NOX BURNER
	 
	10/2/2009
	9
	6.4

	CLEAVER-BROOKS (MODEL CB-700-600-150) BOILER WITH ALZETA 24.5 MMBTU/HR LOW-NOX BURNER
	 
	10/2/2009
	9
	5

	33.6 MMBTU/HR NATURAL GAS-FIRED HURST MODEL S5-X-800-150 BOILER WITH A POWER FLAME MODEL NVC13-G-30 ULTRA LOW NOX BURNER
	 
	10/5/2009
	7
	4.1

	19.95 MMBTU/HR CLEAVER-BROOKS MODEL CB-700-500 NATURAL GAS-FIRED BOILER WITH AN ALZETA MODEL CSB 22-1S0-30 ULTRA LOW NOX BURNER AND FORCED FLUE GAS RECIRCULATION 
	 
	10/6/2009
	9
	7.3

	48 MMBTU/HR CLEAVER BROOKS MODEL D-60 NATURAL GAS-FIRED BOILER WITH CLEAVER BROOKS MODEL PROFIRE NTS LOW NOX BURNER 
	 
	10/9/2009
	9
	7.1

	6.27 MMBTU/HR CLEAVER BROOKS MODEL CB200-150-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-150 ULTRA LOW NOX BURNER
	 
	10/12/2009
	9
	4.6

	11.7 MMBTU/HR CLEAVER BROOKS MODEL CB200X-300-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-300 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	10/12/2009
	9
	5.4

	47.8 MMBTU/HR BABCOCK AND WILCOX NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECH MODEL ACI-04G LOW NOX BURNER WITH INDUCED FLUE GAS RECIRCULATION
	 
	10/12/2009
	9
	8.5

	12.2 MMBTU/HR RAY MODEL 300 EB6012 NATURAL GAS-FIRED BOILER WITH A POWER FLAME MODEL NVC7-G-30 ULTRA LOW NOX BURNER.
	 
	10/12/2009
	9
	5.7

	6.27 MMBTU/HR CLEAVER BROOKS MODEL CB200-150-15ST NATURAL GAS-FIRED BOILER WITH A FIBER-TECH MODEL MFT-150 ULTRA LOW NOX BURNER
	 
	10/13/2009
	9
	6.3

	21.0 MMBTU/HR SUPERIOR MODEL X6X2500S150-M SEMINOLE NATURAL GAS-FIRED BOILER WITH AN AMERICAN COMBUSTION TECHNOLOGY INC MODEL ACT 07-SLE ULTRA LOW NOX BURNER
	 
	10/13/2009
	9
	7.8

	33.6 MMBTU/HR SUPERIOR BOILER MODEL # 6X4000200ACT NATURAL GAS-FIRED AMERICAN COMBUSTION TECHNOLOGY BOILER WITH POWER FLAME MODEL #NVC13-G-30 ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	10/14/2009
	9
	4.4

	62.5 MMBTU/HR NATURAL GAS-FIRED STEAM GENERATOR DIS #22470-79 WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER  AND FLUE GAS RECIRCULATION SYSTEM
	 
	10/20/2009
	7
	6.5

	62 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR) 
	 
	10/20/2009
	7
	6.2

	64.5 MMBTU/HR NATURAL GAS-FIRED BOILER WITH LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	10/21/2009
	8.7
	8.7

	60 MMBTU/HR NEBRASKA MODEL NS-F-89 BOILER WITH AN ALZETA MODEL CSB625R ULTRA LOW NOX BURNER
	 
	10/21/2009
	9
	6

	62.5 MMBTU/HR C.E. NATCO NATURAL GAS FIRED STEAM GENERATOR (#65 DIS# 28623-82) WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM
	 
	10/23/2009
	7
	5.8

	62.5 MMBTU/HR NATURAL GAS/VAPOR RECOVERY GAS FIRED STEAM GENERATOR (#29 DIS# 45004-80) EQUIPPED WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER, AND FLUE GAS RECIRCULATION (FGR)
	 
	10/23/2009
	7
	6

	22.0 MMBTU/HR C.E. NATCO  NATURAL GAS/LPG/PRODUCED GAS/TEOR GAS/WASTE GAS-FIRED STEAM GENERATOR WITH A GIDEON ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION (FGR) OPERATING AT VARIOUS UNSPECIFIED LOCATIONS WITHIN THE E&B HEAVY OIL CENTRAL
	 
	10/28/2009
	9
	8.7

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER AND FGR, APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	11/4/2009
	9
	8

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER AND FGR, APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	11/4/2009
	9
	8

	62.5 MMBTU/HR C.E. NATCO NATURAL GAS FIRED STEAM GENERATOR (#60 DIS# 28618-82) WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER
	 
	11/6/2009
	7
	6.3

	29.92 MMBTU/HR CLEAVER BROOKS MODEL CB-700-700-200 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL INTEGRAL ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	11/13/2009
	9
	7.6

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER, OR DISTRICT APPROVED EQUIVALENT, AND FGR APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	11/17/2009
	9
	7

	62.5 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR DIS #22632-80 WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER  AND FLUE GAS RECIRCULATION SYSTEM  
	 
	11/17/2009
	7
	6.3

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#3) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	11/18/2009
	9
	6.4

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#2) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	11/18/2009
	9
	7.4

	19.9 MMBTU/HR UNIVERSAL BOILER WORKS MODEL #UF-450-W4 NATURAL GAS-FIRED BOILER (#1) WITH AN ACT MODEL #07G-02-SLE ULTRA-LOW NOX BURNER WITH INDUCED FGR AND WITH DIESEL FUEL AS BACKUP
	 
	11/18/2009
	9
	8.4

	11.0 MMBTU/HR TEJAS, TRIPLE S MODEL NATURAL GAS-FIRED BOILER, WITH AN INDUSTRIAL COMBUSTION MODEL NTH110NG-09S-4P ULTRA LOW NOX BURNER, AND INDUCED FGR
	 
	11/19/2009
	9
	8.2

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	11/23/2009
	9
	7.8

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	11/23/2009
	9
	7

	20 MMBTU/HR CLEAVER BROOKS MODEL CBLE (9) 700-500-125HW NATURAL GAS-FIRED BOILER, EQUIPPED WITH ULTRA-LOW NOX BURNER AND A FLUE GAS RECIRCULATION (FGR) SYSTEM AND ALTERNATE EMISSIONS MONITORING PLAN "A"
	 
	11/23/2009
	9
	5.7

	7.971 MMBTU/HR CLAYTON INDUSTRIES MODEL SFG-200M-2-FMB-SSE NATURAL GAS FIRED BOILER.
	 
	12/1/2009
	9
	6.5

	25.2 MMBTU/HR NATURAL GAS/TEOR GAS-FIRED STEAM GENERATOR #4 (DIS #44784-67) WITH NORTH AMERICAN MAGNA-FLAME 4211-25-LE LOW-NOX BURNER WITH FGR AND O2 CONTROLLER (GAMBLE LEASE)
	 
	12/4/2009
	7
	6.4

	62.5 MMBTU/HR NATURAL GAS-FIRED STEAM GENERATOR WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER AND FLUE GAS RECIRCULATION (FGR)  
	 
	12/4/2009
	7
	4.4

	62.5 MMBTU/HR NATURAL GAS/CASING GAS FIRED STEAM GENERATOR (#34 DIS# 45234-82) EQUIPPED WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER  
	 
	12/8/2009
	7
	6.4

	62.5 MMBTU/HR NATURAL GAS/CASING GAS-FIRED STEAM GENERATOR (#37; DIS# 45237-82) WITH O2 CONTROLLER, LOW NOX BURNER, AND FGR APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	12/11/2009
	7
	5.4

	8.4 MMBTU/HR UBW MODEL UFH200-160 BOILER, EQUIPPED WITH A GORDON PIATT MODEL RMB-GO-200 BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	12/15/2009
	9
	9

	14.7 MMBTU/HR UBW MODEL UFH350-160 BOILER, EQUIPPED WITH A GORDON PIATT MODEL RMB-GO-350 BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	12/15/2009
	9
	8.2

	14.7 MMBTU/HR UBW MODEL UFH350-160 BOILER, EQUIPPED WITH A GORDON PIATT MODEL RMB-GO-350 BURNER AND INDUCED FLUE GAS RECIRCULATION
	 
	12/15/2009
	9
	8.5

	7.0 MMBTU/HR NATURAL GAS-FIRED UBW MODEL UFS175150 BOILER EQUIPPED WITH A GORDON PIATT MODEL RMB-GO-175 7.0 MMBTU/HR BURNER AND INDUCED FLUE GAS RECIRCULATION 
	 
	12/16/2009
	9
	8

	24.5 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS BOILER WITH AN IC ULNG-315-P-9 NATURAL GAS ULTRA LOW-NOX BURNER AND FLUE GAS RECIRCULATION (BOILER #2)
	 
	12/17/2009
	7
	4.8

	24.5 MMBTU/HR NATURAL GAS-FIRED CLEAVER BROOKS BOILER WITH IC ULNG-315-P-9 NATURAL GAS ULTRA LOW-NOX BURNER AND FLUE GAS RECIRCULATION (BOILER #1)                           
	 
	12/17/2009
	7
	5.6

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB 1700 500 125 BOILER (NO. 1) WITH A CLEAVER BROOKS MODEL NUMBER NTI-500 LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	12/17/2009
	9
	1.6

	20.9 MMBTU/HR CLEAVER BROOKS MODEL CB 1700 500 125 BOILER (NO. 2) WITH A CLEAVER BROOKS MODEL NUMBER NTI-500 LOW NOX BURNER AND FLUE GAS RECIRCULATION
	 
	12/17/2009
	9
	1.1

	62.5 MMBTU/HR NATURAL GAS/VAPOR RECOVERY GAS-FIRED STEAM GENERATOR (#30 DIS# 45005-80) EQUIPPED WITH A NORTH AMERICAN, MODEL MAGNA-FLAME G-LE, LOW NOX BURNER, A FLUE GAS RECIRCULATION SYSTEM AND AN O2 CONTROLLER
	 
	12/18/2009
	7
	6.6

	12.6 MMBTU/HR CLEAVER BROOKS MODEL 4WI-700X-300-150ST, NATURAL GAS-FIRED BOILER SERVED BY A CLEAVER BROOKS MODEL 4WI700-300-NT9 ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	12/21/2009
	9
	5.8

	12.6 MMBTU/HR CLEAVER BROOKS MODEL 4WI-700X-300-150ST, NATURAL GAS-FIRED BOILER SERVED BY A CLEAVER BROOKS MODEL 4WI700-300-NT9 ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	12/21/2009
	9
	5.7

	62.5 MMBTU/HR NATURAL GAS/TEOR GAS FIRED STEAM GENERATOR (#12 MCKITTRICK FRONT, DIS# 44519-76) EQUIPPED WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION,  AND AN O2 CONTROLLER 
	 
	12/29/2009
	7
	5.8

	19.0 MMBTU/HR NATURAL GAS/PROPANE-FIRED STEAM GENERATOR WITH GIDEON ULTRA LOW NOX BURNER MODEL MGW-25R1 OR EQUIVALENT
	 
	12/30/2009
	9
	9

	30.0 MMBTU/HR NATURAL GAS/PROPANE-FIRED THERMOX STEAM GENERATOR WITH NORTH AMERICAN, MODEL 4211-33/X 4607 LOW NOX BURNER AND FLUE GAS RECIRCULATION (KNAPP LEASE)
	 
	1/8/2010
	7
	6.5

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #1)
	 
	1/12/2010
	9
	8.3

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #2)
	 
	1/12/2010
	9
	7.8

	62.5 MMBTU/HR C.E. NATCO NATURAL GAS FIRED STEAM GENERATOR #59 WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER 
	 
	1/15/2010
	7
	6.5

	16.73 MMBTU/HR CLAYTON INDUSTRIES, MODEL EG404-2-FMB, STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL UH-30672 LOW NOX BURNER
	 
	1/15/2010
	9
	4.9

	62.77 MMBTU/HR CLEAVER BROOKS MODEL CBL700 NATURAL GAS-FIRED BOILER WITH A CLEAVER BROOKS MODEL NTS2-630 ULTRA LOW-NOX BURNER AND FLUE GAS RECIRCULATION (BOILER #4)
	 
	1/19/2010
	7
	5.8

	25.1 MMBTU/HR  CLEAVER BROOKS MODEL CBLE 700-600-150 NATURAL GAS-FIRED BOILER  WITH A CLEAVER BROOKS MODEL CB NTI-9 PPM ULTRA LOW NOX BURNER
	 
	1/20/2010
	9
	6.34

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #3)
	 
	1/26/2010
	9
	7.0

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #4)
	 
	1/26/2010
	9
	7.0

	85.0 MMBTU/HR NATURAL GAS FIRED STEAM GENERATOR WITH NORTH AMERICAN 4231-85-GLE BURNER AND FGR, APPROVED TO OPERATE AT VARIOUS SPECIFIED LOCATIONS
	 
	1/26/2010
	9
	8

	62.5 MMBTU/HR C.E. NATCO NATURAL GAS FIRED STEAM GENERATOR (#58 DIS# 28623-82) WITH A NORTH AMERICAN GLE ULTRA LOW NOX BURNER
	 
	1/29/2010
	7
	6

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #5)
	 
	2/5/2010
	9
	7.55

	8.4 MMBTU/HR CLAYTON INDUSTRIES MODEL SFG-200-M-FMB-1 NATURAL GAS-FIRED STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL 200 FMB ULTRA LOW NOX BURNER
	 
	2/5/2010
	9
	6

	19.98 MMBTU/HR CLEAVER BROOKS MODEL CBI 700-500-150 BOILER 
	 
	2/12/2010
	9
	7.3

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #6)
	 
	2/19/2010
	9
	6.4

	85 MMBTU/HOUR STEAM GENERATOR EQUIPPED WITH NORTH AMERICAN MODEL 4231-85-GLE ULTRA LOW NOX BURNER, FLUE GAS RECIRCULATION (FGR) AND OXYGEN CONTROLLER (SG #7)
	 
	2/19/2010
	9
	7.2

	6.3 MMBTU/HR CLAYTON INDUSTRIES MODEL SFG-150M-1 NATURAL GAS-FIRED STEAM GENERATOR WITH A CLAYTON INDUSTRIES MODEL 150 FMB ULTRA LOW NOX BURNER
	 
	3/2/2010
	9
	8.9

	32.66 MMBTU/HR CLEAVER-BROOKS (BOILER #2) MODEL CB200-800, 150# NATURAL GAS-FIRED BOILER WITH A CLEAVER-BROOKS MODEL PROFIRE NTI-9PPM ULTRA LOW NOX BURNER AND AN INDUCED FLUE GAS RECIRCULATION SYSTEM
	 
	3/3/2010
	9
	7.06

	31.5 MMBTU/HR NATURAL GAS-FIRED HURST BOILER #5 EQUIPPED WITH ULTRA LOW NOX BURNER
	 
	3/9/2010
	7
	5.2

	31.5 MMBTU/HR NATURAL GAS-FIRED HURST BOILER #4 EQUIPPED WITH ULTRA LOW NOX BURNER
	 
	3/9/2010
	7
	5.3

	63 MMBTU/HR HURST SERIES 400 NATURAL GAS FIRED BOILER WITH AN NOVA PLUS ULTRA LOW NOX COMBUSTION SYSTEM MODEL NVC17-G-40 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	3/19/2010
	8.3
	4

	63 MMBTU/HR HURST SERIES 400 NATURAL GAS FIRED BOILER WITH AN NOVA PLUS ULTRA LOW NOX COMBUSTION SYSTEM MODEL NVC17-G-40 ULTRA LOW NOX BURNER AND INDUCED FLUE GAS RECIRCULATION (FGR) SYSTEM
	 
	3/19/2010
	8.3
	4.0


Appendix B
NOx Continuous Emission Monitoring for Boiler with an Ultra-Low NOx Burner and Flue Gas Recirculation 
Note: In the following table “T(f)” is the ambient temperature and
“RH%” is the relative humidity

	
	
	NOx
	
	

	Date
	Hour
	(ppm)
	T(F)
	RH%

	90101
	1
	0.0
	45
	88

	90101
	2
	0.1
	44
	88

	90101
	3
	0.1
	43
	88

	90101
	4
	0.2
	43
	89

	90101
	5
	0.2
	44
	89

	90101
	6
	0.1
	44
	89

	90101
	7
	0.1
	44
	89

	90101
	8
	0.1
	42
	89

	90101
	9
	0.1
	43
	89

	90101
	10
	0.2
	44
	89

	90101
	11
	0.2
	51
	88

	90101
	12
	0.1
	58
	70

	90101
	13
	0.1
	63
	54

	90101
	14
	0.1
	66
	46

	90101
	15
	0.0
	68
	43

	90101
	16
	0.0
	67
	47

	90101
	20
	0.0
	51
	80

	90101
	22
	0.0
	49
	85

	90101
	23
	0.0
	49
	88

	90101
	24
	0.0
	48
	89

	90103
	1
	7.4
	50
	77

	90103
	8
	7.3
	50
	80

	90103
	9
	17.2
	51
	77

	90103
	10
	14.4
	53
	72

	90103
	11
	11.5
	54
	71

	90103
	12
	7.4
	58
	65

	90103
	13
	5.3
	61
	56

	90103
	14
	5.7
	62
	51

	90103
	15
	6.7
	60
	52

	90103
	16
	7.3
	60
	52

	90103
	17
	6.5
	58
	60

	90103
	18
	6.8
	56
	73

	90103
	19
	7.6
	55
	77

	90103
	20
	6.9
	54
	79

	90103
	21
	7.5
	52
	82

	90103
	22
	7.4
	52
	82

	90103
	23
	7.5
	52
	82

	90103
	24
	7.4
	51
	84

	90104
	1
	7.4
	50
	82

	90104
	2
	7.4
	49
	82

	90104
	3
	7.6
	48
	83

	90104
	4
	7.6
	47
	85

	90104
	5
	7.6
	46
	85

	90104
	6
	7.6
	44
	85

	90104
	7
	7.6
	44
	85

	90104
	8
	7.5
	45
	82

	90104
	9
	7.3
	48
	74

	90104
	10
	6.9
	54
	63

	90104
	11
	6.5
	59
	56

	90104
	12
	6.7
	60
	52

	90104
	13
	7.0
	61
	48

	90104
	14
	7.0
	63
	39

	90104
	15
	7.1
	64
	33

	90104
	16
	7.1
	63
	33

	90104
	17
	7.0
	61
	40

	90104
	18
	7.2
	57
	42

	90104
	19
	7.2
	54
	46

	90104
	20
	7.0
	50
	56

	90104
	21
	6.9
	48
	61

	90104
	22
	7.2
	46
	58

	90104
	23
	7.3
	45
	54

	90104
	24
	7.2
	43
	55

	90105
	1
	6.6
	42
	59

	90105
	2
	6.3
	41
	61

	90105
	3
	6.2
	39
	59

	90105
	4
	6.2
	39
	57

	90105
	5
	6.3
	38
	58

	90105
	6
	6.3
	37
	59

	90105
	7
	6.1
	37
	60

	90105
	8
	6.2
	39
	55

	90105
	9
	6.2
	46
	40

	90105
	16
	7.3
	58
	42

	90105
	17
	7.4
	57
	45

	90105
	18
	7.3
	55
	56

	90105
	19
	7.5
	53
	59

	90105
	20
	7.8
	52
	59

	90105
	21
	7.7
	50
	65

	90105
	22
	7.5
	48
	68

	90105
	23
	7.4
	47
	71

	90105
	24
	7.0
	47
	73

	90106
	1
	7.2
	45
	78

	90106
	2
	7.2
	44
	77

	90106
	3
	7.3
	44
	76

	90106
	4
	7.5
	44
	75

	90106
	5
	7.3
	43
	76

	90106
	6
	7.3
	42
	75

	90106
	7
	7.3
	42
	75

	90106
	8
	7.1
	42
	75

	90106
	9
	7.2
	47
	69

	90106
	10
	7.2
	53
	61

	90106
	11
	7.0
	56
	53

	90106
	12
	6.8
	60
	45

	90106
	13
	7.0
	62
	42

	90106
	14
	7.0
	63
	40

	90106
	15
	7.3
	65
	38

	90106
	16
	7.3
	65
	38

	90106
	17
	7.4
	63
	42

	90106
	18
	7.5
	57
	56

	90106
	19
	7.6
	55
	62

	90106
	20
	7.5
	53
	68

	90106
	21
	7.4
	50
	72

	90106
	22
	7.5
	48
	76

	90106
	23
	7.4
	47
	77

	90106
	24
	7.3
	46
	80

	90107
	1
	7.4
	45
	82

	90107
	2
	7.5
	45
	80

	90107
	3
	7.7
	44
	82

	90107
	4
	7.2
	43
	82

	90107
	5
	6.8
	43
	82

	90107
	6
	6.4
	43
	82

	90107
	7
	5.9
	42
	82

	90107
	8
	6.3
	43
	79

	90107
	9
	7.1
	48
	73

	90107
	10
	7.1
	55
	62

	90107
	11
	7.1
	62
	51

	90107
	12
	6.4
	66
	42

	90107
	13
	6.6
	69
	37

	90107
	14
	7.0
	72
	31

	90107
	15
	7.4
	73
	28

	90107
	16
	7.6
	72
	31

	90107
	17
	7.6
	68
	39

	90107
	18
	7.5
	61
	50

	90107
	19
	7.4
	58
	58

	90107
	20
	7.4
	55
	60

	90107
	21
	7.4
	52
	66

	90107
	22
	7.5
	50
	71

	90107
	23
	7.3
	49
	71

	90107
	24
	7.3
	47
	76

	90108
	1
	7.2
	46
	78

	90108
	2
	7.3
	46
	80

	90108
	3
	7.3
	45
	82

	90108
	4
	7.2
	45
	82

	90108
	5
	7.4
	44
	83

	90108
	6
	7.3
	44
	82

	90108
	7
	7.5
	45
	81

	90108
	8
	7.5
	45
	80

	90108
	9
	7.5
	50
	71

	90108
	10
	7.6
	55
	64

	90108
	11
	7.4
	60
	54

	90108
	12
	7.3
	64
	49

	90108
	13
	7.2
	67
	45

	90108
	14
	7.2
	68
	46

	90108
	15
	7.3
	66
	56

	90108
	16
	7.3
	64
	60

	90108
	17
	7.3
	60
	65

	90108
	18
	7.4
	56
	72

	90108
	19
	7.5
	53
	79

	90108
	20
	7.4
	52
	82

	90108
	21
	6.9
	52
	83

	90108
	22
	7.2
	52
	85

	90108
	23
	7.2
	51
	87

	90108
	24
	6.8
	51
	88

	90109
	1
	6.9
	51
	88

	90109
	2
	6.9
	51
	87

	90109
	3
	6.8
	51
	85

	90109
	4
	6.9
	51
	85

	90109
	5
	6.9
	51
	85

	90109
	6
	7.0
	50
	85

	90109
	7
	6.5
	50
	86

	90109
	8
	6.1
	49
	85

	90109
	9
	6.3
	50
	85

	90109
	10
	6.2
	51
	81

	90109
	11
	6.2
	57
	68

	90109
	12
	6.3
	63
	53

	90109
	13
	6.3
	68
	41

	90109
	14
	6.4
	71
	31

	90109
	15
	6.7
	72
	30

	90109
	16
	6.8
	73
	25

	90109
	17
	6.9
	71
	28

	90109
	18
	6.9
	64
	40

	90109
	19
	7.0
	58
	49

	90109
	20
	6.9
	56
	56

	90109
	21
	6.9
	55
	53

	90109
	22
	6.7
	53
	53

	90109
	23
	7.0
	51
	56

	90109
	24
	7.1
	50
	55

	90110
	1
	6.9
	48
	60

	90110
	2
	6.9
	46
	63

	90110
	3
	6.7
	45
	66

	90110
	4
	6.5
	45
	63

	90110
	5
	6.6
	43
	65

	90110
	6
	6.5
	42
	68

	90110
	7
	6.5
	41
	68

	90110
	8
	6.5
	42
	64

	90110
	9
	6.4
	47
	56

	90110
	10
	6.4
	54
	46

	90110
	11
	6.4
	62
	32

	90110
	12
	6.5
	67
	18

	90110
	13
	6.9
	73
	9

	90110
	14
	6.8
	74
	5

	90110
	15
	7.0
	75
	5

	90110
	16
	7.0
	75
	6

	90110
	17
	7.2
	73
	10

	90110
	18
	7.2
	65
	17

	90110
	19
	7.4
	59
	27

	90110
	20
	7.4
	56
	31

	90110
	21
	7.0
	54
	35

	90110
	22
	6.9
	52
	40

	90110
	23
	7.3
	51
	44

	90110
	24
	7.1
	49
	47

	90111
	1
	6.9
	48
	49

	90111
	2
	6.6
	47
	49

	90111
	3
	6.7
	46
	50

	90111
	4
	6.8
	45
	54

	90111
	5
	6.7
	44
	54

	90111
	6
	6.7
	44
	54

	90111
	7
	6.6
	44
	55

	90111
	8
	6.7
	47
	46

	90111
	9
	6.7
	55
	36

	90111
	10
	6.5
	59
	35

	90111
	11
	6.6
	66
	25

	90111
	12
	6.7
	77
	8

	90111
	13
	6.6
	79
	5

	90111
	14
	6.8
	80
	6

	90111
	15
	7.3
	83
	6

	90111
	16
	7.7
	84
	5

	90111
	17
	6.9
	80
	8

	90111
	18
	7.2
	69
	24

	90111
	19
	7.6
	63
	30

	90111
	20
	7.7
	60
	35

	90111
	21
	6.9
	58
	37

	90111
	22
	7.3
	57
	38

	90111
	23
	7.1
	54
	43

	90111
	24
	7.1
	53
	44

	90112
	1
	7.3
	52
	45

	90112
	2
	6.9
	51
	49

	90112
	3
	6.9
	50
	48

	90112
	4
	6.8
	50
	48

	90112
	5
	6.9
	48
	50

	90112
	6
	6.8
	48
	51

	90112
	7
	6.5
	47
	51

	90112
	8
	6.6
	49
	50

	90112
	9
	7.1
	54
	44

	90112
	10
	7.5
	63
	34

	90112
	11
	7.1
	72
	22

	90112
	12
	7.0
	80
	13

	90112
	13
	7.2
	85
	5

	90112
	14
	7.7
	87
	3

	90112
	15
	8.1
	88
	3

	90112
	16
	8.1
	89
	3

	90112
	17
	8.1
	85
	6

	90112
	18
	8.2
	73
	18

	90112
	19
	8.4
	67
	25

	90112
	20
	8.5
	63
	33

	90112
	21
	8.3
	61
	36

	90112
	22
	8.1
	61
	36

	90112
	23
	8.1
	60
	35

	90112
	24
	8.2
	59
	34

	90113
	1
	8.0
	60
	32

	90113
	2
	7.7
	57
	36

	90113
	3
	7.6
	55
	41

	90113
	4
	7.7
	54
	42

	90113
	5
	7.5
	53
	47

	90113
	6
	7.6
	53
	45

	90113
	7
	7.7
	54
	44

	90113
	8
	7.7
	53
	49

	90113
	9
	7.9
	59
	42

	90113
	10
	7.3
	66
	36

	90113
	11
	7.3
	74
	22

	90113
	12
	7.4
	79
	16

	90113
	13
	7.3
	82
	14

	90113
	14
	7.3
	85
	12

	90113
	15
	6.6
	85
	11

	90113
	16
	6.8
	85
	11

	90113
	17
	7.1
	82
	14

	90113
	18
	7.6
	71
	26

	90113
	19
	7.2
	66
	33

	90113
	20
	7.3
	62
	39

	90113
	21
	7.5
	60
	41

	90113
	22
	7.4
	58
	47

	90113
	23
	7.1
	56
	49

	90113
	24
	6.8
	55
	50

	90114
	1
	7.7
	53
	52

	90114
	2
	7.7
	52
	52

	90114
	3
	7.6
	50
	52

	90114
	4
	7.7
	49
	54

	90114
	5
	7.5
	48
	53

	90114
	6
	7.6
	47
	55

	90114
	7
	7.7
	46
	57

	90114
	8
	7.7
	49
	51

	90114
	9
	7.9
	55
	43

	90114
	10
	7.3
	62
	34

	90114
	11
	5.9
	71
	25

	90114
	12
	5.7
	79
	13

	90114
	13
	5.7
	84
	5

	90114
	14
	5.9
	86
	3

	90114
	15
	6.5
	86
	3

	90114
	16
	6.7
	86
	4

	90114
	17
	7.3
	83
	7

	90114
	18
	7.3
	73
	16

	90114
	19
	7.2
	65
	24

	90114
	20
	7.5
	62
	30

	90114
	21
	7.3
	60
	34

	90114
	22
	7.3
	58
	37

	90114
	23
	7.2
	56
	40

	90114
	24
	7.0
	54
	41

	90115
	1
	7.2
	54
	40

	90115
	2
	7.9
	51
	45

	90115
	3
	8.0
	49
	49

	90115
	4
	7.9
	47
	51

	90115
	5
	7.9
	46
	53

	90115
	6
	7.7
	46
	53

	90115
	7
	7.7
	45
	55

	90115
	8
	7.9
	47
	49

	90115
	9
	7.9
	53
	41

	90115
	10
	7.6
	62
	28

	90115
	11
	7.5
	71
	19

	90115
	12
	7.6
	78
	11

	90115
	13
	7.2
	83
	4

	90115
	14
	7.4
	85
	3

	90115
	15
	7.5
	85
	3

	90115
	16
	8.5
	85
	3

	90115
	17
	8.5
	81
	5

	90115
	18
	8.5
	73
	18

	90115
	19
	8.7
	67
	24

	90115
	20
	8.5
	62
	32

	90115
	21
	8.4
	58
	36

	90115
	22
	7.9
	56
	39

	90115
	23
	7.8
	55
	41

	90115
	24
	7.9
	53
	45

	90116
	1
	7.3
	52
	44

	90116
	2
	7.4
	49
	50

	90116
	3
	7.3
	49
	48

	90116
	4
	7.2
	47
	52

	90116
	5
	7.3
	46
	55

	90116
	6
	7.4
	45
	55

	90116
	7
	7.1
	45
	54

	90116
	8
	7.2
	46
	52

	90116
	9
	7.3
	52
	46

	90116
	10
	7.1
	62
	33

	90116
	11
	7.1
	71
	19

	90116
	12
	7.3
	76
	12

	90116
	13
	7.7
	82
	9

	90116
	14
	7.0
	84
	7

	90116
	15
	6.9
	85
	6

	90116
	16
	6.9
	84
	7

	90116
	17
	8.0
	80
	8

	90116
	18
	8.5
	73
	15

	90116
	19
	8.7
	67
	20

	90116
	20
	8.8
	62
	29

	90116
	21
	8.6
	59
	34

	90116
	22
	7.7
	57
	36

	90116
	23
	7.8
	55
	42

	90116
	24
	7.6
	53
	45

	90117
	1
	7.3
	53
	43

	90117
	2
	7.3
	52
	45

	90117
	3
	7.1
	52
	44

	90117
	4
	7.3
	51
	44

	90117
	5
	7.3
	49
	46

	90117
	6
	7.2
	48
	50

	90117
	7
	7.2
	47
	53

	90117
	8
	7.4
	48
	50

	90117
	9
	7.4
	55
	43

	90117
	10
	7.3
	63
	32

	90117
	11
	7.3
	71
	21

	90117
	12
	7.3
	76
	15

	90117
	13
	7.4
	79
	10

	90117
	14
	7.6
	83
	8

	90117
	15
	7.7
	84
	8

	90117
	16
	7.9
	82
	9

	90117
	17
	7.8
	78
	13

	90117
	18
	7.7
	72
	17

	90117
	19
	7.7
	67
	24

	90117
	20
	7.8
	63
	28

	90117
	21
	7.8
	58
	36

	90117
	22
	7.5
	57
	40

	90117
	23
	7.4
	55
	46

	90117
	24
	7.5
	54
	46

	90118
	1
	7.4
	56
	38

	90118
	2
	7.4
	55
	37

	90118
	3
	7.2
	54
	37

	90118
	4
	7.4
	54
	34

	90118
	5
	7.4
	54
	34

	90118
	6
	7.2
	55
	31

	90118
	7
	7.1
	56
	28

	90118
	8
	7.4
	56
	30

	90118
	9
	7.1
	61
	26

	90118
	10
	7.3
	68
	21

	90118
	11
	7.3
	74
	17

	90118
	12
	7.2
	79
	10

	90118
	13
	7.1
	81
	8

	90118
	14
	7.5
	82
	7

	90118
	15
	7.6
	82
	7

	90118
	16
	7.6
	82
	8

	90118
	17
	7.7
	80
	9

	90118
	18
	7.9
	74
	13

	90118
	19
	7.9
	67
	22

	90118
	20
	7.9
	66
	23

	90118
	21
	7.9
	68
	17

	90118
	22
	7.4
	65
	21

	90118
	23
	7.6
	63
	24

	90118
	24
	7.4
	61
	25

	90119
	1
	7.7
	60
	26

	90119
	2
	7.8
	60
	25

	90119
	3
	7.8
	61
	25

	90119
	4
	7.5
	59
	27

	90119
	5
	7.6
	59
	27

	90119
	6
	7.7
	59
	27

	90119
	7
	7.7
	58
	29

	90119
	8
	7.6
	60
	25

	90119
	9
	7.5
	62
	26

	90119
	10
	7.5
	65
	23

	90119
	11
	7.1
	69
	20

	90119
	12
	7.1
	73
	17

	90119
	13
	7.5
	77
	15

	90119
	14
	7.6
	81
	13

	90119
	15
	7.5
	83
	11

	90119
	16
	7.4
	84
	11

	90119
	17
	8.1
	81
	13

	90119
	18
	8.1
	73
	23

	90119
	19
	8.1
	68
	26

	90119
	20
	8.1
	64
	34

	90119
	21
	8.5
	63
	37

	90119
	22
	8.4
	64
	32

	90119
	23
	8.3
	63
	34

	90119
	24
	8.2
	60
	38

	90120
	1
	8.6
	59
	40

	90120
	2
	8.2
	58
	39

	90120
	3
	8.0
	59
	34

	90120
	4
	8.2
	59
	33

	90120
	5
	8.2
	59
	33

	90120
	6
	7.9
	58
	33

	90120
	7
	8.0
	57
	36

	90120
	8
	8.1
	57
	38

	90120
	9
	8.0
	60
	37

	90120
	10
	7.2
	67
	26

	90120
	11
	7.1
	72
	21

	90120
	12
	7.3
	77
	16

	90120
	13
	7.7
	81
	13

	90120
	14
	6.9
	84
	11

	90120
	15
	7.4
	86
	11

	90120
	16
	7.7
	85
	11

	90120
	17
	8.1
	82
	16

	90120
	18
	8.1
	75
	21

	90120
	19
	9.4
	70
	31

	90120
	20
	9.1
	68
	36

	90120
	21
	9.5
	70
	25

	90120
	22
	9.3
	70
	25

	90120
	23
	9.3
	69
	27

	90120
	24
	9.0
	68
	24

	90121
	1
	8.7
	68
	26

	90121
	2
	8.9
	71
	28

	90121
	3
	8.9
	69
	27

	90121
	4
	8.8
	68
	30

	90121
	5
	8.7
	64
	39

	90121
	6
	8.6
	62
	42

	90121
	7
	8.8
	61
	51

	90121
	8
	8.4
	63
	49

	90121
	9
	8.4
	64
	47

	90121
	10
	7.8
	65
	47

	90121
	11
	8.5
	68
	39

	90121
	12
	7.9
	70
	32

	90121
	13
	7.4
	73
	31

	90121
	14
	7.7
	73
	29

	90121
	15
	8.2
	74
	26

	90121
	16
	8.4
	74
	26

	90121
	17
	8.2
	73
	26

	90121
	18
	7.5
	69
	34

	90121
	19
	7.4
	65
	38

	90121
	20
	8.1
	63
	38

	90121
	21
	8.7
	61
	43

	90121
	22
	8.5
	58
	50

	90121
	23
	8.5
	58
	50

	90121
	24
	8.5
	58
	52

	90122
	1
	8.7
	57
	54

	90122
	2
	8.7
	57
	56

	90122
	3
	8.7
	57
	58

	90122
	4
	8.2
	58
	56

	90122
	5
	8.2
	58
	56

	90122
	6
	8.2
	58
	57

	90122
	7
	8.4
	59
	55

	90122
	8
	8.4
	60
	54

	90122
	9
	8.3
	62
	50

	90122
	10
	8.2
	64
	48

	90122
	11
	8.1
	64
	46

	90122
	12
	8.0
	65
	45

	90122
	13
	8.0
	68
	39

	90122
	14
	8.0
	71
	32

	90122
	15
	8.1
	72
	33

	90122
	16
	8.4
	71
	35

	90122
	17
	8.4
	69
	39

	90122
	18
	8.3
	67
	43

	90122
	19
	8.5
	66
	46

	90122
	20
	8.4
	65
	42

	90122
	21
	8.5
	64
	42

	90122
	22
	8.6
	62
	47

	90122
	23
	8.4
	61
	53

	90122
	24
	8.3
	60
	56

	90123
	1
	8.3
	59
	63

	90123
	2
	8.9
	60
	66

	90123
	3
	8.9
	61
	60

	90123
	4
	8.8
	58
	69

	90123
	5
	8.7
	56
	79

	90123
	6
	8.6
	56
	79

	90123
	7
	8.8
	56
	82

	90123
	8
	8.4
	57
	75

	90123
	9
	8.4
	58
	75

	90123
	10
	7.8
	59
	77

	90123
	11
	8.5
	58
	84

	90123
	12
	7.9
	58
	87

	90123
	13
	7.4
	58
	87

	90123
	14
	7.6
	58
	87

	90123
	15
	7.4
	60
	84

	90123
	16
	7.2
	60
	84

	90123
	17
	7.1
	59
	88

	90123
	18
	7.1
	59
	86

	90123
	19
	7.3
	59
	85

	90123
	20
	7.3
	58
	85

	90123
	21
	7.2
	58
	83

	90123
	22
	7.4
	58
	81

	90123
	23
	7.5
	58
	82

	90123
	24
	7.5
	57
	84

	90124
	1
	7.5
	57
	82

	90124
	2
	7.4
	57
	82

	90124
	3
	7.4
	58
	80

	90124
	4
	7.5
	57
	84

	90124
	5
	7.3
	57
	84

	90124
	6
	7.2
	57
	85

	90124
	7
	7.3
	56
	87

	90124
	8
	7.2
	56
	85

	90124
	9
	7.5
	58
	79

	90124
	10
	7.5
	59
	78

	90124
	11
	7.3
	56
	86

	90124
	12
	7.2
	59
	80

	90124
	13
	7.3
	60
	75

	90124
	14
	7.4
	61
	71

	90124
	15
	7.4
	61
	71

	90124
	16
	7.4
	62
	66

	90124
	17
	7.3
	61
	65

	90124
	18
	7.5
	59
	71

	90124
	19
	7.6
	57
	77

	90124
	20
	7.5
	56
	81

	90124
	21
	7.5
	55
	82

	90124
	22
	7.6
	54
	82

	90124
	23
	7.5
	54
	81

	90124
	24
	7.5
	54
	81

	90125
	1
	7.5
	54
	82

	90125
	2
	7.5
	54
	82

	90125
	3
	7.5
	54
	81

	90125
	4
	7.6
	53
	82

	90125
	5
	7.4
	53
	82

	90125
	6
	7.6
	52
	84

	90125
	7
	7.6
	52
	84

	90125
	8
	7.6
	52
	83

	90125
	9
	7.5
	54
	81

	90125
	10
	7.6
	55
	76

	90125
	11
	7.0
	57
	69

	90125
	12
	7.1
	60
	60

	90125
	13
	7.7
	61
	51

	90125
	14
	7.9
	63
	48

	90125
	15
	7.5
	62
	50

	90125
	16
	8.1
	61
	51

	90125
	17
	8.0
	59
	51

	90125
	18
	8.1
	56
	55

	90125
	19
	7.9
	54
	65

	90125
	20
	7.8
	53
	69

	90125
	21
	7.9
	52
	71

	90125
	22
	7.7
	52
	70

	90125
	23
	7.4
	52
	70

	90125
	24
	7.5
	51
	74

	90126
	1
	7.5
	50
	73

	90126
	2
	7.6
	50
	64

	90126
	3
	7.7
	48
	66

	90126
	4
	7.6
	48
	66

	90126
	5
	7.6
	46
	69

	90126
	6
	6.3
	44
	72

	90126
	7
	13.3
	42
	79

	90126
	8
	7.1
	44
	78

	90126
	9
	7.0
	49
	69

	90126
	10
	6.9
	52
	60

	90126
	11
	6.9
	55
	50

	90126
	12
	6.7
	56
	42

	90126
	13
	6.8
	60
	38

	90126
	14
	7.1
	61
	35

	90126
	15
	7.1
	63
	32

	90126
	16
	7.2
	61
	36

	90126
	17
	7.3
	58
	43

	90126
	18
	7.4
	55
	48

	90126
	19
	7.6
	54
	51

	90126
	20
	7.6
	52
	57

	90126
	21
	7.6
	50
	57

	90126
	22
	7.6
	48
	59

	90126
	23
	7.6
	46
	69

	90126
	24
	7.2
	45
	71

	90127
	1
	8.5
	44
	74

	90127
	2
	8.9
	44
	70

	90127
	3
	8.9
	43
	67

	90127
	4
	8.8
	42
	69

	90127
	5
	8.7
	41
	70

	90127
	6
	8.6
	41
	74

	90127
	7
	8.8
	40
	76

	90127
	8
	8.4
	42
	73

	90127
	9
	8.4
	47
	63

	90127
	10
	7.8
	53
	52

	90127
	11
	8.5
	58
	36

	90127
	12
	7.9
	60
	31

	90127
	13
	7.4
	63
	24

	90127
	14
	7.7
	65
	18

	90127
	15
	8.2
	67
	12

	90127
	16
	8.4
	68
	9

	90127
	17
	8.2
	66
	10

	90127
	18
	7.7
	59
	19

	90127
	19
	8.1
	54
	29

	90127
	20
	8.0
	51
	39

	90127
	21
	7.8
	49
	45

	90127
	22
	7.7
	48
	49

	90127
	23
	7.5
	47
	53

	90127
	24
	7.8
	45
	57

	90128
	1
	7.7
	44
	59

	90128
	2
	7.6
	43
	61

	90128
	3
	7.6
	42
	62

	90128
	4
	7.6
	41
	61

	90128
	5
	7.5
	41
	61

	90128
	6
	7.5
	41
	58

	90128
	7
	7.5
	40
	58

	90128
	8
	7.4
	42
	55

	90128
	9
	7.6
	50
	40

	90128
	10
	7.6
	57
	28

	90128
	11
	7.8
	64
	20

	90128
	12
	7.9
	67
	14

	90128
	13
	8.1
	70
	9

	90128
	14
	8.1
	72
	8

	90128
	15
	8.5
	74
	9

	90128
	16
	8.3
	76
	10

	90128
	17
	8.6
	74
	11

	90128
	18
	8.7
	66
	32

	90128
	19
	9.0
	61
	42

	90128
	20
	9.1
	58
	52

	90128
	21
	8.8
	54
	53

	90128
	22
	8.4
	53
	53

	90128
	23
	8.4
	51
	60

	90128
	24
	8.1
	49
	61

	90129
	1
	8.3
	48
	61

	90129
	2
	8.1
	46
	65

	90129
	3
	7.8
	45
	66

	90129
	4
	7.7
	44
	68

	90129
	5
	7.6
	44
	68

	90129
	6
	7.7
	43
	70

	90129
	7
	7.7
	44
	66

	90129
	8
	7.8
	46
	62

	90129
	9
	8.0
	52
	53

	90129
	10
	8.2
	60
	43

	90129
	11
	8.0
	70
	24

	90129
	12
	8.1
	76
	12

	90129
	13
	8.3
	79
	8

	90129
	14
	8.5
	81
	4

	90129
	15
	8.6
	84
	3

	90129
	16
	8.7
	83
	3

	90129
	17
	8.7
	79
	7

	90129
	18
	8.6
	73
	15

	90129
	19
	8.7
	66
	21

	90129
	20
	8.9
	62
	28

	90129
	21
	9.0
	58
	33

	90129
	22
	8.7
	56
	37

	90129
	23
	8.7
	53
	41

	90129
	24
	8.7
	52
	41

	90130
	1
	8.5
	49
	47

	90130
	2
	8.6
	48
	50

	90130
	3
	8.4
	47
	50

	90130
	4
	8.4
	46
	53

	90130
	5
	8.2
	45
	58

	90130
	6
	8.2
	44
	59

	90130
	7
	8.4
	44
	59

	90130
	8
	8.4
	46
	54

	90130
	9
	8.4
	54
	43

	90130
	10
	8.4
	62
	31

	90130
	11
	8.1
	71
	19

	90130
	12
	8.0
	76
	14

	90130
	13
	8.5
	80
	7

	90130
	14
	8.6
	81
	6

	90130
	15
	8.6
	81
	6

	90130
	16
	8.7
	81
	7

	90130
	17
	8.7
	79
	12

	90130
	18
	8.8
	73
	15

	90130
	19
	9.0
	67
	22

	90130
	20
	8.8
	61
	31

	90130
	21
	8.8
	59
	37

	90130
	22
	8.8
	58
	39

	90130
	23
	8.7
	56
	42

	90130
	24
	8.5
	55
	43

	90131
	1
	8.3
	54
	43

	90131
	2
	8.4
	53
	44

	90131
	3
	8.4
	52
	43

	90131
	4
	8.5
	51
	45

	90131
	5
	8.5
	50
	59

	90131
	6
	8.5
	49
	51

	90131
	7
	8.4
	48
	51

	90131
	8
	8.4
	50
	50

	90131
	9
	8.3
	56
	41

	90131
	10
	8.4
	63
	33

	90131
	11
	8.4
	71
	22

	90131
	12
	8.4
	76
	16

	90131
	13
	5.8
	78
	13

	90131
	14
	5.3
	79
	12

	90131
	15
	7.5
	80
	11

	90131
	16
	44.7
	78
	15

	90131
	17
	8.9
	74
	22

	90131
	18
	8.7
	68
	27

	90131
	19
	8.6
	64
	29

	90131
	20
	8.6
	61
	33

	90131
	21
	8.6
	56
	42

	90131
	22
	8.4
	54
	46

	90131
	23
	8.3
	52
	50

	90131
	24
	8.3
	50
	52

	90201
	1
	8.2
	49
	54

	90201
	2
	8.3
	48
	58

	90201
	3
	8.1
	47
	65

	90201
	4
	7.9
	46
	65

	90201
	5
	7.9
	47
	74

	90201
	6
	7.8
	45
	82

	90201
	7
	7.2
	43
	87

	90201
	8
	7.2
	44
	88

	90201
	9
	7.3
	50
	75

	90201
	10
	7.4
	58
	47

	90201
	11
	7.5
	65
	36

	90201
	12
	7.6
	70
	28

	90201
	13
	7.8
	72
	24

	90201
	14
	8.2
	75
	22

	90201
	15
	8.3
	75
	30

	90201
	16
	8.2
	72
	42

	90201
	17
	8.2
	71
	46

	90201
	18
	8.1
	66
	54

	90201
	19
	8.3
	62
	60

	90201
	20
	8.3
	59
	65

	90201
	21
	8.2
	57
	68

	90201
	22
	8.3
	55
	72

	90201
	23
	8.0
	53
	76

	90201
	24
	7.9
	52
	79

	90202
	1
	8.2
	50
	81

	90202
	2
	8.2
	49
	80

	90202
	3
	8.2
	49
	78

	90202
	4
	8.0
	47
	72

	90202
	5
	8.1
	46
	70

	90202
	6
	8.1
	47
	60

	90202
	7
	8.3
	46
	56

	90202
	8
	8.2
	49
	46

	90202
	9
	8.2
	57
	38

	90202
	10
	8.2
	65
	25

	90202
	11
	7.9
	72
	17

	90202
	12
	8.1
	77
	11

	90202
	13
	8.2
	80
	7

	90202
	14
	8.6
	82
	5

	90202
	15
	8.7
	82
	3

	90202
	16
	8.7
	84
	3

	90202
	17
	8.0
	81
	6

	90202
	18
	8.2
	74
	14

	90202
	19
	8.6
	68
	19

	90202
	20
	8.5
	63
	27

	90202
	21
	8.5
	59
	34

	90202
	22
	8.7
	57
	38

	90202
	23
	8.6
	55
	43

	90202
	24
	8.7
	53
	46

	90203
	1
	8.9
	52
	49

	90203
	2
	8.5
	51
	48

	90203
	3
	8.5
	50
	48

	90203
	4
	8.2
	50
	44

	90203
	5
	8.1
	50
	43

	90203
	6
	7.9
	51
	38

	90203
	7
	8.1
	51
	36

	90203
	8
	8.3
	54
	35

	90203
	9
	8.1
	60
	28

	90203
	10
	8.4
	66
	19

	90203
	11
	8.4
	72
	13

	90203
	12
	7.7
	78
	8

	90203
	13
	7.7
	83
	5

	90203
	14
	7.9
	83
	3

	90203
	15
	8.1
	83
	3

	90203
	16
	8.5
	83
	3

	90203
	17
	8.3
	80
	5

	90203
	18
	9.2
	75
	7

	90203
	19
	9.3
	68
	15

	90203
	20
	9.7
	63
	23

	90203
	21
	9.5
	59
	29

	90203
	22
	9.2
	57
	31

	90203
	23
	9.5
	54
	39

	90203
	24
	9.6
	53
	44

	90204
	1
	9.2
	53
	44

	90204
	2
	9.2
	52
	45

	90204
	3
	9.3
	50
	50

	90204
	4
	9.2
	50
	50

	90204
	5
	9.1
	48
	50

	90204
	6
	8.9
	50
	44

	90204
	7
	8.5
	51
	39

	90204
	8
	8.3
	53
	38

	90204
	9
	8.7
	63
	25

	90204
	10
	8.4
	71
	15

	90204
	11
	7.9
	75
	14

	90204
	12
	7.8
	80
	13

	90204
	13
	7.7
	80
	7

	90204
	14
	7.9
	80
	7

	90204
	15
	8.3
	80
	8

	90204
	16
	8.5
	-1
	-1

	90204
	17
	8.5
	72
	9

	90204
	18
	8.9
	67
	14

	90204
	19
	8.8
	63
	20

	90204
	20
	8.6
	59
	25

	90204
	21
	8.5
	59
	28

	90204
	22
	9.0
	56
	33

	90204
	23
	8.8
	55
	35

	90204
	24
	8.7
	55
	35

	90207
	1
	8.2
	51
	84

	90207
	2
	8.2
	51
	83

	90207
	3
	8.4
	51
	82

	90207
	4
	8.2
	50
	78

	90207
	5
	8.3
	50
	77

	90207
	6
	8.5
	50
	74

	90207
	7
	8.2
	50
	72

	90207
	8
	8.3
	50
	76

	90207
	9
	7.9
	52
	73

	90207
	10
	7.7
	51
	77

	90207
	11
	7.5
	50
	82

	90207
	12
	7.6
	52
	75

	90207
	13
	7.9
	55
	62

	90207
	14
	7.5
	58
	54

	90207
	15
	7.1
	60
	50

	90207
	16
	7.7
	59
	51

	90207
	17
	7.9
	57
	57

	90207
	18
	8.0
	56
	61

	90207
	19
	8.0
	54
	67

	90207
	20
	8.3
	53
	70

	90207
	21
	7.9
	51
	80

	90207
	22
	7.5
	49
	84

	90207
	23
	7.5
	49
	84

	90207
	24
	8.4
	49
	84

	90209
	1
	8.0
	-1
	-1

	90209
	2
	8.2
	50
	79

	90209
	3
	8.2
	50
	82

	90209
	4
	8.2
	50
	76

	90209
	5
	7.0
	-1
	-1

	90209
	6
	7.5
	49
	85

	90209
	7
	7.7
	-1
	-1

	90209
	8
	8.2
	-1
	-1

	90209
	9
	8.5
	52
	71

	90209
	10
	8.3
	-1
	-1

	90209
	11
	7.9
	-1
	-1

	90209
	12
	7.1
	-1
	-1

	90209
	13
	6.7
	-1
	-1

	90209
	14
	7.2
	-1
	-1

	90209
	15
	7.3
	-1
	-1

	90209
	16
	7.4
	50
	59

	90209
	17
	7.6
	51
	53

	90209
	18
	7.6
	51
	44

	90209
	19
	7.8
	50
	36

	90209
	20
	7.9
	48
	42

	90209
	21
	7.9
	48
	41

	90209
	22
	7.7
	48
	41

	90209
	23
	7.6
	47
	41

	90209
	24
	7.6
	46
	44

	90211
	1
	7.6
	41
	74

	90211
	8
	7.4
	41
	73

	90211
	9
	7.6
	45
	64

	90211
	10
	7.6
	50
	56

	90211
	11
	7.4
	55
	48

	90211
	12
	7.3
	58
	44

	90211
	13
	7.4
	59
	40

	90211
	14
	7.5
	60
	38

	90211
	15
	6.7
	60
	41

	90211
	16
	6.4
	59
	41

	90211
	17
	7.5
	57
	45

	90211
	18
	8.0
	54
	58

	90211
	19
	7.8
	53
	65

	90211
	20
	7.5
	53
	68

	90211
	21
	7.4
	51
	77

	90211
	22
	7.4
	51
	80

	90211
	23
	7.9
	51
	80

	90211
	24
	7.8
	50
	80

	90212
	1
	8.0
	48
	84

	90212
	2
	7.9
	46
	85

	90212
	3
	8.0
	44
	87

	90212
	4
	8.0
	43
	88

	90212
	5
	7.9
	43
	87

	90212
	6
	8.0
	42
	87

	90212
	7
	7.9
	41
	87

	90212
	8
	8.0
	44
	81

	90212
	9
	7.9
	50
	72

	90212
	10
	7.5
	52
	67

	90212
	11
	7.7
	55
	56

	90212
	12
	7.7
	58
	39

	90212
	13
	7.9
	60
	30

	90212
	14
	8.2
	59
	36

	90212
	15
	8.0
	59
	38

	90212
	16
	7.8
	59
	40

	90212
	17
	7.7
	58
	41

	90212
	18
	7.8
	56
	47

	90212
	19
	8.4
	54
	58

	90212
	20
	8.4
	52
	64

	90212
	21
	8.0
	51
	63

	90212
	22
	8.1
	49
	66

	90212
	23
	8.1
	46
	72

	90212
	24
	8.2
	45
	74

	90213
	1
	8.1
	45
	77

	90213
	2
	8.1
	45
	74

	90213
	3
	7.9
	44
	75

	90213
	4
	8.0
	43
	75

	90213
	5
	8.0
	43
	75

	90213
	6
	8.0
	44
	73

	90213
	7
	8.0
	43
	72

	90213
	8
	8.2
	44
	77

	90213
	9
	8.3
	47
	80

	90213
	10
	8.0
	49
	77

	90213
	11
	7.8
	51
	73

	90213
	12
	7.9
	53
	67

	90213
	13
	8.0
	53
	58

	90213
	14
	8.3
	51
	63

	90213
	15
	8.1
	48
	79

	90213
	16
	8.2
	47
	79

	90213
	17
	8.2
	48
	76

	90213
	18
	8.3
	48
	76

	90213
	19
	7.9
	47
	78

	90213
	20
	7.9
	47
	80

	90213
	21
	7.9
	46
	80

	90213
	22
	7.8
	44
	83

	90213
	23
	7.9
	42
	83

	90213
	24
	7.9
	42
	82

	90214
	1
	7.8
	42
	83

	90214
	2
	7.8
	41
	84

	90214
	3
	7.9
	40
	85

	90214
	4
	7.9
	39
	85

	90214
	5
	7.9
	38
	85

	90214
	6
	7.9
	38
	85

	90214
	7
	7.8
	37
	86

	90214
	8
	7.9
	38
	87

	90214
	9
	7.8
	43
	83

	90214
	10
	7.9
	50
	68

	90214
	11
	7.9
	54
	54

	90214
	12
	7.8
	55
	50

	90214
	13
	7.5
	57
	43

	90214
	14
	7.2
	58
	40

	90214
	15
	7.4
	59
	36

	90214
	16
	7.9
	58
	41

	90214
	17
	7.7
	56
	49

	90214
	18
	7.6
	53
	52

	90214
	19
	7.9
	51
	56

	90214
	20
	8.0
	48
	63

	90214
	21
	8.1
	46
	70

	90214
	22
	7.9
	44
	73

	90214
	23
	7.8
	43
	76

	90214
	24
	7.8
	43
	77

	90215
	1
	7.9
	42
	79

	90215
	2
	7.9
	41
	79

	90215
	3
	7.8
	40
	79

	90215
	4
	7.6
	40
	80

	90215
	5
	7.5
	40
	80

	90215
	6
	7.4
	40
	80

	90215
	7
	7.4
	39
	81

	90215
	8
	7.4
	41
	77

	90215
	9
	7.3
	47
	68

	90215
	10
	7.3
	53
	57

	90215
	11
	7.3
	57
	51

	90215
	12
	7.5
	59
	45

	90215
	13
	7.6
	59
	44

	90215
	14
	7.7
	59
	42

	90215
	15
	7.8
	60
	43

	90215
	16
	8.1
	59
	45

	90215
	17
	8.0
	58
	48

	90215
	18
	8.1
	55
	53

	90215
	19
	7.8
	53
	59

	90215
	20
	7.9
	51
	67

	90215
	21
	7.9
	50
	72

	90215
	22
	7.8
	49
	73

	90215
	23
	7.6
	48
	76

	90215
	24
	7.6
	49
	76

	90216
	1
	7.7
	48
	77

	90216
	2
	7.6
	47
	76

	90216
	3
	7.6
	51
	62

	90216
	4
	7.7
	51
	63

	90216
	5
	7.8
	49
	71

	90216
	6
	8.1
	48
	78

	90216
	7
	8.2
	47
	80

	90216
	8
	7.9
	46
	85

	90216
	9
	8.0
	47
	84

	90216
	10
	8.3
	47
	85

	90216
	11
	7.6
	50
	84

	90216
	12
	7.5
	53
	85

	90216
	13
	7.4
	56
	82

	90216
	14
	7.3
	54
	77

	90216
	15
	7.9
	56
	69

	90216
	16
	7.9
	57
	64

	90216
	17
	7.9
	56
	62

	90216
	18
	7.8
	54
	62

	90216
	19
	8.1
	52
	62

	90216
	20
	8.0
	50
	68

	90216
	21
	8.0
	49
	78

	90216
	22
	7.7
	48
	81

	90216
	23
	7.9
	46
	85

	90216
	24
	8.1
	46
	85

	90217
	1
	7.8
	45
	86

	90217
	2
	7.9
	44
	87

	90217
	3
	8.0
	44
	87

	90217
	4
	8.0
	46
	86

	90217
	5
	7.9
	46
	87

	90217
	6
	8.0
	46
	86

	90217
	7
	8.0
	46
	85

	90217
	8
	8.1
	47
	81

	90217
	9
	7.2
	46
	81

	90217
	10
	7.2
	49
	77

	90217
	11
	7.4
	52
	69

	90217
	12
	7.3
	55
	61

	90217
	13
	7.4
	58
	53

	90217
	14
	7.7
	58
	51

	90217
	15
	7.5
	57
	54

	90217
	16
	7.4
	56
	55

	90217
	17
	7.5
	56
	54

	90217
	18
	7.7
	56
	52

	90217
	19
	7.6
	55
	62

	90217
	20
	7.6
	53
	69

	90217
	21
	7.5
	51
	72

	90217
	22
	7.5
	50
	77

	90217
	23
	7.3
	50
	78

	90217
	24
	7.3
	49
	82

	90219
	1
	5.7
	47
	69

	90219
	2
	7.6
	47
	66

	90219
	3
	7.5
	46
	67

	90219
	4
	7.4
	45
	67

	90219
	5
	7.5
	44
	67

	90219
	6
	8.4
	44
	64

	90219
	7
	13.9
	44
	63

	90219
	8
	6.0
	47
	60

	90219
	9
	0.0
	54
	46

	90219
	11
	0.0
	66
	27

	90219
	15
	7.7
	76
	13

	90219
	16
	20.5
	77
	13

	90219
	17
	19.0
	74
	18

	90219
	18
	25.8
	69
	25

	90219
	19
	2.9
	64
	28

	90219
	20
	0.1
	60
	30

	90219
	22
	0.1
	53
	45

	90219
	23
	0.1
	52
	50

	90219
	24
	0.1
	53
	49

	90220
	1
	0.2
	50
	54

	90220
	2
	0.1
	50
	52

	90220
	3
	0.1
	49
	52

	90220
	4
	0.1
	48
	53

	90220
	5
	0.1
	48
	53

	90220
	6
	0.1
	46
	56

	90220
	7
	0.1
	46
	56

	90220
	8
	0.1
	49
	52

	90220
	9
	0.0
	57
	39

	90220
	10
	0.1
	63
	30

	90220
	11
	0.1
	67
	25

	90220
	12
	13.7
	72
	21

	90220
	13
	8.8
	75
	16

	90220
	14
	11.6
	77
	11

	90220
	15
	0.5
	77
	8

	90220
	16
	6.8
	77
	11

	90220
	17
	4.8
	71
	22

	90220
	18
	18.8
	66
	27

	90220
	19
	12.4
	62
	35

	90220
	20
	3.3
	58
	42

	90220
	21
	0.2
	56
	47

	90220
	22
	0.2
	54
	50

	90220
	23
	0.2
	51
	59

	90220
	24
	0.3
	51
	61

	90222
	1
	0.3
	59
	58

	90222
	8
	0.0
	56
	68

	90222
	9
	0.1
	57
	68

	90222
	10
	0.1
	59
	65

	90222
	11
	0.1
	62
	57

	90222
	12
	0.1
	65
	49

	90222
	13
	0.0
	67
	43

	90222
	18
	0.0
	66
	48

	90222
	19
	0.0
	65
	49

	90222
	20
	0.1
	63
	53

	90222
	21
	0.1
	62
	54

	90222
	22
	0.2
	62
	55

	90222
	23
	0.2
	60
	60

	90222
	24
	0.2
	60
	63

	90223
	1
	0.2
	59
	67

	90223
	2
	0.1
	58
	67

	90223
	3
	0.3
	57
	70

	90223
	4
	0.2
	57
	69

	90223
	5
	0.2
	58
	69

	90223
	6
	0.2
	58
	70

	90223
	7
	0.2
	58
	72

	90223
	8
	0.2
	59
	70

	90223
	9
	0.4
	61
	66

	90223
	10
	0.4
	67
	54

	90223
	11
	0.4
	69
	51

	90223
	12
	0.2
	70
	51

	90223
	13
	0.0
	70
	51

	90223
	14
	0.1
	73
	47

	90223
	15
	0.1
	74
	46

	90223
	16
	0.0
	74
	42

	90223
	18
	0.0
	69
	56

	90223
	19
	0.0
	64
	61

	90223
	20
	0.0
	62
	64

	90223
	21
	0.0
	60
	68

	90223
	22
	0.0
	58
	71

	90223
	23
	0.1
	58
	73

	90223
	24
	0.1
	55
	77

	90224
	1
	2.1
	53
	80

	90224
	2
	0.1
	52
	82

	90224
	3
	0.1
	51
	84

	90224
	4
	0.1
	50
	85

	90224
	5
	0.2
	49
	85

	90224
	6
	0.2
	49
	84

	90224
	7
	0.3
	48
	84

	90224
	8
	0.4
	51
	78

	90224
	9
	8.3
	58
	70

	90224
	10
	7.8
	62
	66

	90224
	11
	7.2
	66
	59

	90224
	12
	7.3
	69
	51

	90224
	13
	9.0
	70
	46

	90224
	14
	8.9
	70
	47

	90224
	15
	8.5
	70
	42

	90224
	16
	8.5
	70
	43

	90224
	17
	8.7
	69
	42

	90224
	18
	8.6
	66
	50

	90224
	19
	8.3
	62
	58

	90224
	20
	8.4
	60
	61

	90224
	21
	8.5
	58
	70

	90224
	22
	8.1
	56
	77

	90224
	23
	8.0
	55
	78

	90224
	24
	8.2
	54
	79

	90225
	1
	8.2
	53
	83

	90225
	2
	8.1
	52
	86

	90225
	3
	8.1
	53
	82

	90225
	4
	8.2
	53
	79

	90225
	5
	8.1
	53
	78

	90225
	6
	8.3
	54
	75

	90225
	7
	8.4
	54
	71

	90225
	8
	8.4
	55
	69

	90225
	9
	8.5
	55
	69

	90225
	10
	8.2
	57
	64

	90225
	11
	7.9
	58
	62

	90225
	12
	7.8
	61
	55

	90225
	13
	7.6
	65
	48

	90225
	14
	7.9
	65
	47

	90225
	15
	7.9
	65
	46

	90225
	16
	8.2
	63
	53

	90225
	17
	8.3
	62
	56

	90225
	18
	8.3
	60
	58

	90225
	19
	8.4
	57
	61

	90225
	20
	8.3
	56
	68

	90225
	21
	8.3
	55
	71

	90225
	22
	8.4
	53
	75

	90225
	23
	8.2
	52
	78

	90225
	24
	8.1
	50
	80

	90226
	1
	8.1
	49
	82

	90226
	2
	8.3
	49
	83

	90226
	3
	8.3
	48
	84

	90226
	4
	8.3
	47
	85

	90226
	5
	8.3
	47
	85

	90226
	6
	8.0
	46
	85

	90226
	7
	8.1
	47
	84

	90226
	8
	8.2
	50
	79

	90226
	9
	8.2
	55
	72

	90226
	10
	7.9
	58
	66

	90226
	11
	7.7
	61
	59

	90226
	12
	7.9
	64
	55

	90226
	13
	7.9
	65
	52

	90226
	14
	8.1
	65
	56

	90226
	15
	8.3
	63
	62

	90226
	16
	8.3
	63
	60

	90226
	17
	8.4
	63
	60

	90226
	18
	7.8
	61
	61

	90226
	19
	7.8
	58
	71

	90226
	20
	8.2
	57
	74

	90226
	21
	8.3
	56
	76

	90226
	22
	8.3
	55
	79

	90226
	23
	8.3
	54
	81

	90226
	24
	8.3
	53
	82

	90227
	1
	8.4
	54
	80

	90227
	2
	8.2
	55
	77

	90227
	3
	8.0
	55
	77

	90227
	4
	8.2
	54
	78

	90227
	5
	8.3
	52
	82

	90227
	6
	8.4
	52
	83

	90227
	7
	8.3
	52
	83

	90227
	8
	8.2
	54
	80

	90227
	9
	7.9
	58
	74

	90227
	10
	7.9
	58
	71

	90227
	11
	7.9
	62
	61

	90227
	12
	7.9
	64
	54

	90227
	13
	8.0
	66
	52

	90227
	14
	8.3
	68
	47

	90227
	15
	8.4
	69
	44

	90227
	16
	8.5
	70
	42

	90227
	17
	8.6
	65
	58

	90227
	18
	8.5
	62
	64

	90227
	19
	8.7
	59
	64

	90227
	20
	8.7
	57
	68

	90227
	21
	8.6
	56
	73

	90227
	22
	8.3
	54
	76

	90227
	23
	8.3
	52
	79

	90227
	24
	8.3
	52
	81

	90228
	1
	8.5
	52
	80

	90228
	2
	8.8
	51
	81

	90228
	3
	8.6
	51
	81

	90228
	4
	8.5
	50
	80

	90228
	5
	8.6
	49
	81

	90228
	6
	8.5
	50
	76

	90228
	7
	8.5
	51
	71

	90228
	8
	8.6
	56
	60

	90228
	9
	8.4
	64
	44

	90228
	10
	8.3
	69
	34

	90228
	11
	8.5
	75
	25

	90228
	12
	8.5
	79
	20

	90228
	13
	9.0
	84
	15

	90228
	14
	9.1
	85
	12

	90228
	15
	9.6
	86
	11

	90228
	16
	9.5
	86
	9

	90228
	17
	9.3
	85
	6

	90228
	18
	9.3
	77
	27

	90228
	19
	9.0
	70
	32

	90228
	20
	8.7
	68
	35

	90228
	21
	8.3
	65
	40

	90228
	22
	8.2
	61
	44

	90228
	23
	8.3
	59
	50

	90228
	24
	8.3
	58
	54

	90301
	1
	8.1
	57
	57

	90301
	2
	8.0
	57
	57

	90301
	3
	8.0
	57
	55

	90301
	4
	8.0
	56
	51

	90301
	5
	8.4
	59
	42

	90301
	6
	8.1
	60
	38

	90301
	7
	8.1
	59
	41

	90301
	8
	8.2
	62
	41

	90301
	9
	8.3
	67
	36

	90301
	10
	8.3
	75
	27

	90301
	11
	8.2
	80
	23

	90301
	12
	8.2
	81
	19

	90301
	13
	8.3
	83
	16

	90301
	14
	8.7
	80
	22

	90301
	15
	8.5
	80
	20

	90301
	16
	8.7
	80
	18

	90301
	17
	8.7
	76
	22

	90301
	18
	8.8
	73
	25

	90301
	19
	9.0
	69
	31

	90301
	20
	8.9
	67
	34

	90301
	21
	8.7
	64
	40

	90301
	22
	8.5
	63
	42

	90301
	23
	8.4
	59
	50

	90301
	24
	8.1
	58
	54

	90303
	1
	7.7
	58
	75

	90303
	8
	7.5
	56
	82

	90303
	9
	7.5
	59
	76

	90303
	10
	7.5
	64
	64

	90303
	11
	7.4
	66
	53

	90303
	12
	7.7
	67
	50

	90303
	13
	7.9
	67
	47

	90303
	14
	8.0
	68
	36

	90303
	15
	7.8
	68
	33

	90303
	16
	8.3
	68
	33

	90303
	17
	8.2
	64
	44

	90303
	18
	8.0
	61
	52

	90303
	19
	7.7
	59
	55

	90303
	20
	8.0
	57
	56

	90303
	21
	8.0
	56
	57

	90303
	22
	7.9
	54
	65

	90303
	23
	7.9
	51
	72

	90303
	24
	8.0
	51
	76

	90304
	1
	7.9
	50
	80

	90304
	2
	7.9
	49
	82

	90304
	3
	7.9
	48
	84

	90304
	4
	7.8
	47
	82

	90304
	5
	7.9
	46
	79

	90304
	6
	7.8
	47
	79

	90304
	7
	7.8
	48
	76

	90304
	8
	7.8
	51
	79

	90304
	9
	7.9
	52
	81

	90304
	10
	7.8
	51
	83

	90304
	11
	7.7
	52
	83

	90304
	12
	7.2
	55
	77

	90304
	13
	6.9
	55
	80

	90304
	14
	6.9
	55
	83

	90304
	15
	6.8
	56
	81

	90304
	16
	6.6
	56
	83

	90304
	17
	6.9
	57
	75

	90304
	18
	6.8
	56
	73

	90304
	19
	7.2
	56
	75

	90304
	20
	7.5
	55
	78

	90304
	21
	7.6
	54
	83

	90304
	22
	8.1
	53
	86

	90304
	23
	7.9
	51
	87

	90304
	24
	7.8
	49
	87

	90306
	1
	8.1
	45
	76

	90306
	2
	8.0
	44
	77

	90306
	3
	8.0
	43
	79

	90306
	4
	8.0
	43
	77

	90306
	5
	7.9
	42
	76

	90306
	6
	7.9
	42
	77

	90306
	7
	7.9
	44
	74

	90306
	8
	7.9
	48
	69

	90306
	9
	8.0
	52
	62

	90306
	10
	7.6
	56
	58

	90306
	11
	0.4
	59
	53

	90306
	12
	0.3
	60
	49

	90306
	13
	6.3
	62
	44

	90306
	14
	0.4
	61
	49

	90306
	17
	5.6
	58
	48

	90306
	18
	8.0
	57
	51

	90306
	19
	8.1
	55
	62

	90306
	20
	7.8
	54
	68

	90306
	21
	8.1
	53
	71

	90306
	22
	8.4
	52
	74

	90306
	23
	9.0
	51
	75

	90306
	24
	8.6
	50
	78

	90307
	1
	8.6
	48
	81

	90307
	2
	8.6
	48
	80

	90307
	3
	8.4
	48
	77

	90307
	4
	8.6
	48
	78

	90307
	5
	8.6
	48
	77

	90307
	6
	8.4
	48
	77

	90307
	7
	8.3
	48
	76

	90307
	8
	8.3
	52
	69

	90307
	9
	8.4
	54
	64

	90307
	10
	8.0
	57
	58

	90307
	11
	8.0
	60
	48

	90307
	12
	8.0
	63
	43

	90307
	13
	8.0
	64
	40

	90307
	14
	8.1
	66
	36

	90307
	15
	8.0
	67
	36

	90307
	16
	8.3
	65
	42

	90307
	17
	8.3
	63
	51

	90307
	18
	8.6
	60
	53

	90307
	19
	8.8
	57
	62

	90307
	20
	8.8
	55
	68

	90307
	21
	9.2
	54
	70

	90307
	22
	9.1
	53
	73

	90307
	23
	8.7
	51
	75

	90307
	24
	8.7
	49
	78

	90308
	1
	8.6
	48
	78

	90308
	2
	8.4
	47
	80

	90308
	3
	8.4
	47
	83

	90308
	4
	8.6
	46
	82

	90308
	5
	8.5
	45
	82

	90308
	6
	8.3
	44
	83

	90308
	7
	8.4
	45
	81

	90308
	8
	8.5
	48
	76

	90308
	9
	8.5
	53
	71

	90308
	10
	8.1
	60
	62

	90308
	11
	7.8
	61
	57

	90308
	12
	7.9
	62
	55

	90308
	13
	8.0
	64
	50

	90308
	14
	8.1
	65
	50

	90308
	15
	7.7
	63
	54

	90308
	16
	8.2
	63
	54

	90308
	17
	8.4
	62
	56

	90308
	18
	8.3
	60
	58

	90308
	19
	8.6
	57
	59

	90308
	20
	8.6
	55
	59

	90308
	21
	8.7
	54
	63

	90308
	22
	8.6
	55
	63

	90308
	23
	8.3
	55
	64

	90308
	24
	8.4
	55
	63

	90310
	1
	8.5
	52
	64

	90310
	2
	8.5
	51
	64

	90310
	3
	8.5
	50
	67

	90310
	4
	8.3
	48
	70

	90310
	5
	8.1
	46
	73

	90310
	6
	7.9
	45
	76

	90310
	7
	8.1
	46
	74

	90310
	8
	7.4
	50
	67

	90310
	9
	7.2
	54
	60

	90310
	10
	7.6
	55
	58

	90310
	11
	7.9
	60
	49

	90310
	12
	7.7
	61
	46

	90310
	13
	7.6
	64
	41

	90310
	14
	8.1
	65
	38

	90310
	15
	8.6
	67
	34

	90310
	16
	8.3
	65
	41

	90310
	17
	7.8
	63
	45

	90310
	18
	7.6
	59
	53

	90310
	19
	7.7
	56
	57

	90310
	20
	8.0
	55
	54

	90310
	21
	8.4
	54
	58

	90310
	22
	8.1
	51
	65

	90310
	23
	8.1
	50
	68

	90310
	24
	8.1
	48
	70

	90311
	1
	7.8
	47
	75

	90311
	2
	7.8
	46
	76

	90311
	3
	7.8
	45
	77

	90311
	4
	8.1
	45
	80

	90311
	5
	8.4
	45
	80

	90311
	6
	8.5
	44
	79

	90311
	7
	8.1
	45
	79

	90311
	8
	6.9
	49
	74

	90311
	9
	9.6
	53
	68

	90311
	10
	6.1
	56
	63

	90311
	11
	6.1
	58
	57

	90311
	12
	6.4
	61
	53

	90311
	13
	6.3
	61
	51

	90311
	14
	6.5
	61
	54

	90311
	15
	6.8
	61
	53

	90311
	16
	7.2
	61
	53

	90311
	17
	7.3
	59
	53

	90311
	18
	7.2
	56
	57

	90311
	19
	7.3
	55
	58

	90311
	20
	7.1
	55
	57

	90311
	21
	7.1
	54
	59

	90311
	22
	7.2
	54
	61

	90311
	23
	7.5
	53
	63

	90311
	24
	7.4
	53
	65

	90312
	1
	7.1
	53
	65

	90312
	2
	7.1
	53
	65

	90312
	3
	6.9
	53
	66

	90312
	4
	7.2
	53
	67

	90312
	5
	7.4
	52
	68

	90312
	6
	7.2
	51
	72

	90312
	7
	7.3
	52
	70

	90312
	8
	7.0
	56
	63

	90312
	9
	6.9
	59
	56

	90312
	10
	6.7
	59
	53

	90312
	11
	6.9
	60
	50

	90312
	12
	6.8
	63
	46

	90312
	13
	5.7
	63
	45

	90312
	14
	5.5
	64
	43

	90312
	15
	6.1
	64
	41

	90312
	16
	6.4
	62
	43

	90312
	17
	6.6
	61
	44

	90312
	18
	6.7
	59
	47

	90312
	19
	6.8
	57
	51

	90312
	20
	6.8
	55
	59

	90312
	21
	10.3
	53
	65

	90312
	22
	8.9
	51
	70

	90312
	23
	6.0
	50
	72

	90312
	24
	6.8
	48
	75

	90314
	1
	6.8
	54
	80

	90314
	2
	6.9
	54
	77

	90314
	3
	6.8
	54
	74

	90314
	4
	7.1
	54
	73

	90314
	5
	7.4
	54
	73

	90314
	6
	7.3
	54
	72

	90314
	7
	7.3
	54
	72

	90314
	8
	7.4
	54
	71

	90314
	9
	7.3
	55
	70

	90314
	10
	7.2
	55
	71

	90314
	11
	7.0
	56
	68

	90314
	12
	7.0
	57
	66

	90314
	13
	7.1
	60
	60

	90314
	14
	7.2
	63
	55

	90314
	15
	7.0
	64
	52

	90314
	16
	7.1
	63
	55

	90314
	17
	7.2
	61
	59

	90314
	18
	7.0
	58
	63

	90314
	19
	7.2
	57
	66

	90314
	20
	7.0
	56
	69

	90314
	21
	7.2
	56
	70

	90314
	22
	7.0
	56
	70

	90314
	23
	6.9
	55
	71

	90314
	24
	7.0
	55
	69

	90315
	1
	7.1
	53
	72

	90315
	2
	7.4
	53
	74

	90315
	3
	7.1
	54
	72

	90315
	4
	7.0
	54
	71

	90315
	5
	7.1
	54
	72

	90315
	6
	7.2
	53
	74

	90315
	7
	7.1
	54
	75

	90315
	8
	7.1
	54
	74

	90315
	9
	7.0
	56
	70

	90315
	10
	6.8
	57
	62

	90315
	11
	6.6
	59
	57

	90315
	12
	6.3
	59
	55

	90315
	13
	7.0
	61
	53

	90315
	14
	7.0
	62
	51

	90315
	15
	7.1
	63
	49

	90315
	16
	7.1
	63
	49

	90315
	17
	7.1
	62
	50

	90315
	18
	7.1
	60
	53

	90315
	19
	7.2
	57
	58

	90315
	20
	7.1
	56
	63

	90315
	21
	7.1
	53
	67

	90315
	22
	6.9
	51
	72

	90315
	23
	6.9
	50
	75

	90315
	24
	7.1
	49
	77

	90318
	1
	7.3
	56
	71

	90318
	2
	7.4
	55
	70

	90318
	3
	7.3
	55
	70

	90318
	4
	7.4
	53
	75

	90318
	5
	7.4
	52
	77

	90318
	6
	7.3
	51
	79

	90318
	7
	7.3
	53
	76

	90318
	8
	7.1
	59
	66

	90318
	9
	6.9
	64
	57

	90318
	10
	6.9
	71
	47

	90318
	11
	7.2
	76
	39

	90318
	12
	7.5
	80
	36

	90318
	13
	7.8
	84
	31

	90318
	14
	7.8
	85
	25

	90318
	15
	8.0
	86
	23

	90318
	16
	8.0
	85
	27

	90318
	17
	8.3
	84
	27

	90318
	18
	8.3
	78
	35

	90318
	19
	8.2
	71
	41

	90318
	20
	8.0
	67
	47

	90318
	21
	7.8
	65
	50

	90318
	22
	7.8
	63
	63

	90318
	23
	7.7
	61
	73

	90318
	24
	7.3
	58
	79

	90320
	1
	7.1
	55
	83

	90320
	2
	7.1
	55
	83

	90320
	3
	7.1
	54
	83

	90320
	4
	7.1
	54
	83

	90320
	5
	7.3
	54
	82

	90320
	6
	7.7
	55
	81

	90320
	7
	8.4
	55
	80

	90320
	11
	0.0
	63
	64

	90320
	12
	0.0
	67
	57

	90320
	13
	0.0
	69
	53

	90320
	14
	0.0
	68
	54

	90320
	15
	0.0
	67
	57

	90320
	17
	0.0
	65
	57

	90323
	1
	0.1
	48
	39

	90323
	5
	0.0
	41
	63

	90323
	6
	0.0
	40
	65

	90323
	7
	0.1
	42
	63

	90323
	8
	7.8
	48
	53

	90323
	9
	0.5
	54
	40

	90323
	10
	0.2
	59
	32

	90323
	11
	0.1
	61
	25

	90323
	12
	0.1
	63
	20

	90323
	13
	0.0
	66
	18

	90323
	15
	0.0
	70
	15

	90323
	16
	0.1
	67
	19

	90323
	17
	0.0
	66
	27

	90323
	21
	0.0
	53
	47

	90323
	23
	0.0
	50
	54

	90323
	24
	0.1
	49
	61

	90324
	1
	1.9
	48
	66

	90324
	2
	0.1
	48
	60

	90324
	3
	0.1
	46
	67

	90324
	4
	0.1
	45
	65

	90324
	5
	0.1
	45
	67

	90324
	6
	0.2
	45
	66

	90324
	7
	9.9
	47
	60

	90324
	8
	8.2
	53
	49

	90324
	9
	5.8
	62
	30

	90324
	10
	5.5
	69
	20

	90324
	11
	6.5
	71
	15

	90324
	12
	6.8
	73
	12

	90324
	13
	7.2
	76
	8

	90324
	14
	7.4
	77
	7

	90324
	15
	7.8
	76
	9

	90324
	16
	7.9
	74
	11

	90324
	17
	7.8
	72
	15

	90324
	18
	7.8
	70
	15

	90324
	19
	8.0
	66
	24

	90324
	20
	8.0
	62
	34

	90324
	21
	7.6
	60
	37

	90324
	22
	7.4
	56
	41

	90324
	23
	7.5
	53
	47

	90324
	24
	7.6
	52
	51

	90325
	1
	7.4
	51
	56

	90325
	2
	7.5
	50
	60

	90325
	3
	7.7
	50
	57

	90325
	4
	7.5
	49
	55

	90325
	5
	7.5
	49
	55

	90325
	6
	7.6
	48
	55

	90325
	7
	7.6
	50
	53

	90325
	8
	7.7
	57
	41

	90325
	9
	7.5
	64
	30

	90325
	10
	7.6
	68
	26

	90325
	11
	7.4
	70
	25

	90325
	12
	7.2
	73
	21

	90325
	13
	7.4
	76
	18

	90325
	14
	7.5
	78
	18

	90325
	15
	7.7
	77
	23

	90325
	16
	7.8
	75
	22

	90325
	17
	7.8
	72
	22

	90325
	18
	7.7
	69
	26

	90325
	19
	7.7
	66
	31

	90325
	20
	7.9
	64
	38

	90325
	21
	7.9
	61
	52

	90325
	22
	7.9
	59
	62

	90325
	23
	7.4
	57
	60

	90325
	24
	7.1
	55
	64

	90327
	1
	7.1
	53
	76

	90327
	2
	7.0
	53
	77

	90327
	3
	6.9
	53
	79

	90327
	4
	6.8
	52
	82

	90327
	5
	7.0
	51
	84

	90327
	6
	7.0
	50
	85

	90327
	7
	7.1
	52
	83

	90327
	8
	6.7
	56
	77

	90327
	9
	6.7
	62
	66

	90327
	10
	6.6
	69
	44

	90327
	11
	6.8
	71
	32

	90327
	12
	7.1
	75
	23

	90327
	13
	7.4
	77
	18

	90327
	14
	7.8
	79
	16

	90327
	15
	7.5
	78
	17

	90327
	16
	7.1
	75
	19

	90327
	17
	6.8
	72
	23

	90327
	18
	7.7
	69
	26

	90327
	19
	7.1
	67
	24

	90327
	20
	7.4
	65
	29

	90327
	21
	7.5
	62
	36

	90327
	22
	7.2
	60
	43

	90327
	23
	7.1
	57
	52

	90327
	24
	7.1
	56
	52

	90330
	1
	7.4
	55
	75

	90330
	2
	7.4
	55
	73

	90330
	3
	7.4
	55
	72

	90330
	4
	7.3
	55
	71

	90330
	5
	7.3
	55
	71

	90330
	6
	7.4
	55
	72

	90330
	7
	7.4
	55
	70

	90330
	8
	7.3
	57
	68

	90330
	9
	7.1
	59
	63

	90330
	10
	7.4
	62
	56

	90330
	11
	7.6
	66
	47

	90330
	12
	7.4
	68
	42

	90330
	13
	7.5
	70
	36

	90330
	14
	7.6
	71
	31

	90330
	15
	7.6
	73
	28

	90330
	16
	7.7
	72
	31

	90330
	17
	8.0
	71
	31

	90330
	18
	8.1
	67
	37

	90330
	19
	8.1
	64
	30

	90330
	20
	8.2
	62
	35

	90330
	21
	8.1
	58
	41

	90330
	22
	8.1
	59
	39

	90330
	23
	7.9
	58
	45

	90330
	24
	7.6
	56
	64

	90331
	1
	7.5
	55
	72

	90331
	2
	7.4
	54
	73

	90331
	3
	7.4
	52
	70

	90331
	4
	7.4
	50
	73

	90331
	5
	7.3
	49
	76

	90331
	6
	7.4
	49
	76

	90331
	7
	7.5
	52
	75

	90331
	8
	7.4
	58
	60

	90331
	9
	7.2
	63
	50

	90331
	10
	6.8
	65
	49

	90331
	11
	6.7
	68
	44

	90331
	12
	7.1
	71
	34

	90331
	13
	7.2
	74
	28

	90331
	14
	7.5
	74
	35

	90331
	15
	8.0
	74
	25

	90331
	16
	8.4
	72
	23

	90331
	17
	8.5
	70
	26

	90331
	18
	8.6
	66
	33

	90331
	19
	8.7
	63
	39

	90331
	20
	8.8
	61
	48

	90331
	21
	8.7
	58
	52

	90331
	22
	8.6
	57
	57

	90331
	23
	8.5
	56
	71

	90331
	24
	8.2
	55
	80

	90401
	1
	8.2
	54
	81

	90401
	2
	8.2
	53
	79

	90401
	3
	7.9
	52
	80

	90401
	4
	7.8
	51
	82

	90401
	5
	7.9
	51
	79

	90401
	6
	8.3
	51
	72

	90401
	7
	8.3
	53
	70

	90401
	8
	8.1
	56
	70

	90401
	9
	7.8
	59
	63

	90401
	10
	7.5
	62
	57

	90401
	11
	6.8
	64
	51

	90401
	12
	7.5
	68
	44

	90401
	13
	7.8
	69
	46

	90401
	14
	7.8
	67
	53

	90401
	15
	8.0
	67
	53

	90401
	16
	8.1
	67
	51

	90401
	17
	8.0
	66
	51

	90401
	18
	8.1
	64
	54

	90401
	19
	8.1
	61
	60

	90401
	20
	7.7
	59
	62

	90401
	21
	8.4
	58
	66

	90401
	22
	8.5
	57
	70

	90401
	23
	8.5
	55
	73

	90401
	24
	8.3
	54
	75

	90402
	1
	8.3
	53
	77

	90402
	2
	7.9
	52
	79

	90402
	3
	7.9
	53
	78

	90402
	4
	7.8
	55
	76

	90402
	5
	8.0
	56
	76

	90402
	6
	8.1
	56
	76

	90402
	7
	8.0
	56
	76

	90402
	8
	8.1
	57
	73

	90402
	9
	8.2
	58
	71

	90402
	10
	8.5
	59
	70

	90402
	11
	8.1
	61
	66

	90402
	12
	8.0
	62
	64

	90402
	13
	7.9
	64
	60

	90402
	14
	7.9
	64
	60

	90402
	15
	8.0
	63
	61

	90402
	16
	7.9
	61
	63

	90402
	17
	8.2
	60
	64

	90402
	18
	8.4
	59
	65

	90402
	19
	8.1
	59
	66

	90402
	20
	8.0
	58
	68

	90402
	21
	8.1
	58
	70

	90402
	22
	7.8
	57
	70

	90402
	23
	7.9
	57
	72

	90402
	24
	8.2
	57
	74

	90403
	1
	8.3
	56
	78

	90403
	2
	8.4
	55
	81

	90403
	3
	8.1
	55
	81

	90403
	4
	7.8
	55
	80

	90403
	5
	8.4
	55
	78

	90403
	6
	8.3
	55
	78

	90403
	7
	8.2
	55
	75

	90403
	8
	8.3
	57
	72

	90403
	9
	8.2
	58
	68

	90403
	10
	7.9
	61
	61

	90403
	11
	7.9
	63
	55

	90403
	12
	7.9
	64
	51

	90403
	13
	8.0
	64
	49

	90403
	14
	8.2
	63
	50

	90403
	15
	8.0
	65
	46

	90403
	16
	7.9
	64
	44

	90403
	17
	8.2
	64
	39

	90403
	18
	7.8
	62
	43

	90403
	19
	7.6
	58
	60

	90403
	20
	8.7
	56
	66

	90403
	21
	8.6
	55
	69

	90403
	22
	8.4
	54
	71

	90403
	23
	8.1
	53
	73

	90403
	24
	8.2
	52
	74

	90405
	1
	8.4
	51
	52

	90405
	2
	7.7
	51
	54

	90405
	3
	8.2
	50
	54

	90405
	4
	7.8
	49
	54

	90405
	5
	7.7
	49
	49

	90405
	6
	8.1
	49
	42

	90405
	7
	8.3
	53
	37

	90405
	8
	8.2
	58
	32

	90405
	9
	8.0
	65
	21

	90405
	10
	7.7
	72
	9

	90405
	11
	8.3
	76
	6

	90405
	12
	8.7
	78
	4

	90405
	13
	8.4
	80
	3

	90405
	14
	9.0
	82
	4

	90405
	15
	9.0
	82
	3

	90405
	16
	9.1
	80
	5

	90405
	17
	9.0
	78
	7

	90405
	18
	9.2
	76
	8

	90405
	19
	9.0
	72
	11

	90405
	20
	9.3
	66
	17

	90405
	21
	9.3
	62
	26

	90405
	22
	8.6
	60
	32

	90405
	23
	9.4
	58
	35

	90405
	24
	9.4
	57
	39

	90406
	1
	8.7
	55
	42

	90406
	2
	9.1
	53
	45

	90406
	3
	9.0
	53
	46

	90406
	4
	8.8
	52
	44

	90406
	5
	8.7
	52
	46

	90406
	6
	8.5
	50
	49

	90406
	7
	8.2
	55
	41

	90406
	8
	8.0
	63
	26

	90406
	9
	8.1
	69
	18

	90406
	10
	7.3
	76
	12

	90406
	11
	7.6
	82
	6

	90406
	12
	7.4
	84
	4

	90406
	13
	8.1
	84
	4

	90406
	14
	8.3
	84
	4

	90406
	15
	8.0
	83
	3

	90406
	16
	8.3
	83
	3

	90406
	17
	8.3
	82
	8

	90406
	18
	8.3
	78
	11

	90406
	19
	8.3
	70
	30

	90406
	20
	8.1
	66
	40

	90406
	21
	7.2
	63
	45

	90406
	22
	7.4
	61
	48

	90406
	23
	7.4
	57
	48

	90406
	24
	7.1
	55
	45

	90407
	1
	7.2
	53
	50

	90407
	2
	7.2
	53
	56

	90407
	3
	7.2
	51
	63

	90407
	4
	7.3
	50
	66

	90407
	5
	6.9
	49
	74

	90407
	6
	7.0
	49
	72

	90407
	7
	7.2
	52
	67

	90407
	8
	7.2
	56
	77

	90407
	9
	7.4
	61
	65

	90407
	10
	7.2
	64
	54

	90407
	11
	7.3
	67
	47

	90407
	12
	7.2
	68
	45

	90407
	13
	6.9
	69
	39

	90407
	14
	7.0
	71
	35

	90407
	15
	7.3
	70
	38

	90407
	16
	7.6
	69
	38

	90407
	17
	7.3
	66
	44

	90407
	18
	7.1
	62
	56

	90407
	19
	7.2
	60
	66

	90407
	20
	7.2
	59
	73

	90407
	21
	7.1
	59
	73

	90407
	22
	7.3
	58
	75

	90407
	23
	7.3
	57
	76

	90407
	24
	7.0
	55
	77

	90408
	1
	6.7
	56
	75

	90408
	2
	7.0
	55
	73

	90408
	3
	7.1
	55
	78

	90408
	4
	7.0
	54
	76

	90408
	5
	7.1
	53
	79

	90408
	6
	7.4
	52
	81

	90408
	7
	7.4
	56
	73

	90408
	8
	7.1
	60
	64

	90408
	9
	7.1
	59
	59

	90408
	10
	6.9
	62
	48

	90408
	11
	6.9
	63
	45

	90408
	12
	7.0
	64
	43

	90408
	13
	7.0
	64
	42

	90408
	14
	7.0
	64
	40

	90408
	15
	7.1
	63
	43

	90408
	16
	7.0
	63
	45

	90408
	17
	7.1
	62
	46

	90408
	18
	7.3
	60
	54

	90408
	19
	7.2
	58
	57

	90408
	20
	7.0
	57
	64

	90408
	21
	7.0
	56
	70

	90408
	22
	7.1
	55
	73

	90408
	23
	7.1
	54
	74

	90408
	24
	7.0
	53
	76

	90409
	1
	7.0
	52
	78

	90409
	2
	6.8
	51
	80

	90409
	3
	6.8
	50
	80

	90409
	4
	6.8
	50
	80

	90409
	5
	6.8
	51
	79

	90409
	6
	6.9
	52
	78

	90409
	7
	6.9
	54
	74

	90409
	8
	6.9
	57
	68

	90409
	9
	6.8
	59
	61

	90409
	10
	6.8
	60
	57

	90409
	11
	6.8
	62
	52

	90409
	12
	7.0
	64
	48

	90409
	13
	6.9
	67
	44

	90409
	14
	7.1
	67
	45

	90409
	15
	7.1
	66
	47

	90409
	16
	7.2
	64
	51

	90409
	17
	7.1
	62
	59

	90409
	18
	7.2
	60
	63

	90409
	19
	7.5
	58
	67

	90409
	20
	7.6
	57
	69

	90409
	21
	7.5
	56
	70

	90409
	22
	7.3
	55
	72

	90409
	23
	7.4
	54
	73

	90409
	24
	7.5
	54
	72

	90410
	1
	7.3
	54
	73

	90410
	2
	7.4
	54
	74

	90410
	3
	7.6
	54
	74

	90410
	4
	7.4
	54
	74

	90410
	5
	7.4
	54
	74

	90410
	6
	7.3
	54
	73

	90410
	7
	7.5
	55
	71

	90410
	8
	7.6
	56
	68

	90410
	9
	7.5
	59
	63

	90410
	10
	7.4
	60
	59

	90410
	11
	7.1
	59
	57

	90410
	12
	7.3
	59
	55

	90410
	13
	7.3
	60
	53

	90410
	14
	7.5
	61
	51

	90410
	15
	7.3
	61
	51

	90410
	16
	7.4
	61
	49

	90410
	17
	7.6
	60
	47

	90410
	18
	7.5
	59
	52

	90410
	19
	7.6
	58
	62

	90410
	20
	7.4
	56
	69

	90410
	21
	7.5
	56
	69

	90410
	22
	7.4
	55
	72

	90410
	23
	7.4
	53
	75

	90410
	24
	7.3
	52
	77

	90413
	1
	7.1
	53
	77

	90413
	2
	7.2
	52
	79

	90413
	3
	7.1
	51
	80

	90413
	4
	7.1
	51
	81

	90413
	5
	7.2
	51
	82

	90413
	6
	7.3
	51
	82

	90413
	7
	8.0
	54
	77

	90413
	8
	0.1
	59
	69

	90413
	9
	0.0
	66
	57

	90413
	11
	0.0
	72
	45

	90413
	12
	0.1
	75
	37

	90413
	13
	0.0
	78
	32

	90413
	14
	0.0
	78
	32

	90413
	15
	0.0
	77
	35

	90413
	23
	0.0
	58
	73

	90414
	2
	0.0
	57
	71

	90414
	3
	0.0
	56
	76

	90414
	4
	0.0
	56
	79

	90414
	8
	0.0
	61
	70

	90414
	13
	0.1
	66
	54

	90416
	6
	0.0
	44
	75

	90416
	7
	0.0
	47
	68

	90416
	8
	0.1
	52
	61

	90416
	9
	0.0
	57
	55

	90416
	11
	0.0
	63
	44

	90416
	15
	0.3
	66
	33

	90416
	16
	4.5
	66
	26

	90416
	17
	0.1
	64
	30

	90418
	1
	7.7
	53
	57

	90418
	2
	7.7
	52
	61

	90418
	3
	7.7
	51
	68

	90418
	4
	7.8
	51
	71

	90418
	5
	7.6
	50
	69

	90418
	6
	7.8
	51
	64

	90418
	7
	7.8
	56
	58

	90418
	8
	7.8
	64
	45

	90418
	9
	7.8
	72
	32

	90418
	10
	7.7
	77
	26

	90418
	11
	7.7
	79
	21

	90418
	12
	7.8
	82
	17

	90418
	13
	7.9
	84
	16

	90418
	14
	8.1
	85
	16

	90418
	15
	8.4
	83
	16

	90418
	16
	8.2
	82
	16

	90418
	17
	8.1
	79
	17

	90418
	18
	7.8
	76
	20

	90418
	19
	7.8
	73
	25

	90418
	20
	7.8
	69
	32

	90418
	21
	7.6
	66
	40

	90418
	22
	7.2
	64
	46

	90418
	23
	7.0
	61
	50

	90418
	24
	7.1
	59
	49

	90419
	1
	7.4
	58
	57

	90419
	2
	7.2
	57
	58

	90419
	3
	7.1
	57
	57

	90419
	4
	7.2
	55
	57

	90419
	5
	7.2
	58
	48

	90419
	6
	7.3
	58
	50

	90419
	7
	7.5
	61
	47

	90419
	8
	7.7
	69
	37

	90419
	9
	7.5
	78
	25

	90419
	10
	7.6
	84
	16

	90419
	11
	7.9
	89
	10

	90419
	12
	8.0
	94
	6

	90419
	13
	8.2
	96
	4

	90419
	14
	8.4
	97
	3

	90419
	15
	8.3
	98
	4

	90419
	16
	8.2
	93
	8

	90419
	17
	8.4
	90
	9

	90419
	18
	8.5
	88
	10

	90419
	19
	8.7
	83
	14

	90419
	20
	8.6
	79
	19

	90419
	21
	8.0
	76
	23

	90419
	22
	8.0
	72
	31

	90419
	23
	8.2
	69
	36

	90419
	24
	8.0
	67
	42

	90420
	1
	8.4
	65
	42

	90420
	2
	8.2
	66
	40

	90420
	3
	8.3
	65
	40

	90420
	4
	8.4
	63
	44

	90420
	5
	8.3
	62
	44

	90420
	6
	8.3
	63
	41

	90420
	7
	8.4
	69
	35

	90420
	8
	8.4
	76
	26

	90420
	9
	8.1
	83
	19

	90420
	10
	8.3
	91
	11

	90420
	11
	8.6
	95
	7

	90420
	12
	8.7
	99
	5

	90420
	13
	8.7
	99
	4

	90420
	14
	8.5
	99
	3

	90420
	15
	8.6
	98
	3

	90420
	16
	8.5
	98
	3

	90420
	17
	8.4
	96
	3

	90420
	18
	8.5
	94
	3

	90420
	19
	8.6
	90
	5

	90420
	20
	8.6
	85
	9

	90420
	21
	8.5
	80
	16

	90420
	22
	8.5
	76
	23

	90420
	23
	8.3
	74
	29

	90420
	24
	8.4
	72
	33

	90421
	1
	8.1
	70
	36

	90421
	2
	8.3
	69
	37

	90421
	3
	8.3
	68
	38

	90421
	4
	8.1
	68
	35

	90421
	5
	8.2
	67
	37

	90421
	6
	8.3
	67
	35

	90421
	7
	8.1
	71
	34

	90421
	8
	8.0
	78
	24

	90421
	9
	7.8
	87
	15

	90421
	10
	7.5
	89
	15

	90421
	11
	7.8
	90
	16

	90421
	12
	7.8
	93
	11

	90421
	13
	7.8
	95
	14

	90421
	14
	8.2
	95
	13

	90421
	15
	8.4
	95
	9

	90421
	16
	7.7
	92
	10

	90421
	17
	7.7
	90
	9

	90421
	18
	7.7
	85
	17

	90421
	19
	7.9
	78
	29

	90421
	20
	7.7
	74
	38

	90421
	21
	7.6
	68
	58

	90421
	22
	7.5
	65
	64

	90421
	23
	7.3
	64
	65

	90421
	24
	7.3
	63
	66

	90422
	1
	7.6
	62
	68

	90422
	2
	7.4
	61
	74

	90422
	3
	7.4
	60
	74

	90422
	4
	7.3
	60
	73

	90422
	5
	7.4
	59
	74

	90422
	6
	7.5
	59
	75

	90422
	7
	7.3
	62
	75

	90422
	8
	7.4
	63
	74

	90422
	9
	7.4
	65
	68

	90422
	10
	7.4
	68
	62

	90422
	11
	7.5
	71
	56

	90422
	12
	7.3
	72
	55

	90422
	13
	7.3
	72
	53

	90422
	14
	7.3
	72
	53

	90422
	15
	7.5
	70
	57

	90422
	16
	7.6
	70
	56

	90422
	17
	7.8
	70
	54

	90422
	18
	7.8
	67
	61

	90422
	19
	8.0
	63
	69

	90422
	20
	8.0
	59
	76

	90422
	21
	7.9
	58
	78

	90422
	22
	7.7
	58
	77

	90422
	23
	7.6
	58
	76

	90422
	24
	7.5
	59
	75

	90423
	1
	7.5
	59
	73

	90423
	2
	7.1
	58
	72

	90423
	3
	7.2
	58
	73

	90423
	4
	7.4
	58
	72

	90423
	5
	7.1
	58
	73

	90423
	6
	7.2
	57
	76

	90423
	7
	7.1
	57
	76

	90423
	8
	7.2
	58
	74

	90423
	9
	7.4
	59
	69

	90423
	10
	7.4
	61
	65

	90423
	11
	7.1
	63
	61

	90423
	12
	7.1
	63
	62

	90423
	13
	7.1
	65
	59

	90423
	14
	6.9
	68
	52

	90423
	15
	6.9
	68
	53

	90423
	16
	7.1
	69
	53

	90423
	17
	7.3
	66
	59

	90423
	18
	7.3
	63
	65

	90423
	19
	7.3
	60
	72

	90423
	20
	7.3
	59
	73

	90423
	21
	7.3
	59
	72

	90423
	22
	7.6
	59
	72

	90423
	23
	7.9
	58
	71

	90423
	24
	7.9
	58
	72

	90424
	1
	7.6
	59
	72

	90424
	2
	7.8
	59
	70

	90424
	3
	7.9
	59
	71

	90424
	4
	7.4
	58
	73

	90424
	5
	7.4
	58
	74

	90424
	6
	7.1
	58
	73

	90424
	7
	7.9
	58
	70

	90428
	1
	0.0
	56
	63

	90428
	2
	0.0
	56
	62

	90428
	3
	0.0
	56
	64

	90428
	4
	0.0
	54
	68

	90428
	5
	0.0
	52
	71

	90428
	6
	0.1
	54
	69

	90428
	7
	0.1
	56
	65

	90428
	8
	0.1
	57
	61

	90428
	9
	0.1
	59
	56

	90428
	10
	0.1
	63
	48

	90428
	14
	0.3
	66
	44

	90429
	1
	7.5
	51
	72

	90429
	7
	7.3
	56
	66

	90429
	8
	13.9
	58
	62

	90429
	9
	8.7
	60
	57

	90429
	10
	5.7
	62
	51

	90429
	11
	5.8
	63
	48

	90429
	12
	6.6
	66
	43

	90429
	13
	7.1
	69
	39

	90429
	14
	6.8
	69
	45

	90429
	15
	6.6
	68
	48

	90429
	16
	6.7
	67
	49

	90429
	17
	7.0
	65
	52

	90429
	18
	7.3
	63
	54

	90429
	19
	7.5
	59
	54

	90429
	20
	7.5
	58
	53

	90429
	21
	7.6
	58
	54

	90429
	22
	7.5
	57
	59

	90429
	23
	7.4
	55
	62

	90429
	24
	7.5
	53
	65

	90430
	1
	7.4
	52
	67

	90430
	2
	7.2
	51
	68

	90430
	3
	7.2
	50
	69

	90430
	4
	7.3
	50
	71

	90430
	5
	7.4
	50
	74

	90430
	6
	7.4
	55
	74

	90430
	7
	7.5
	-1
	66

	90430
	8
	7.4
	60
	58

	90430
	9
	7.1
	65
	51

	90430
	10
	6.8
	66
	47

	90430
	11
	6.8
	69
	41

	90430
	12
	7.0
	72
	37

	90430
	13
	6.9
	74
	38

	90430
	14
	6.8
	72
	43

	90430
	15
	7.0
	71
	42

	90430
	16
	7.1
	72
	41

	90430
	17
	6.9
	70
	43

	90430
	18
	7.1
	67
	48

	90430
	19
	7.1
	64
	51

	90430
	20
	7.3
	63
	51

	90430
	21
	7.4
	61
	58

	90430
	22
	7.3
	60
	61

	90430
	23
	7.1
	59
	63

	90430
	24
	7.1
	57
	66

	90501
	1
	7.1
	57
	69

	90501
	2
	7.0
	56
	72

	90501
	3
	7.1
	55
	73

	90501
	4
	7.0
	54
	74

	90501
	5
	7.0
	54
	74

	90501
	6
	6.8
	55
	75

	90501
	7
	6.7
	58
	70

	90501
	8
	7.0
	62
	62

	90501
	9
	7.2
	68
	53

	90501
	10
	7.1
	72
	48

	90501
	11
	7.1
	74
	45

	90501
	12
	7.1
	73
	44

	90501
	13
	7.3
	71
	50

	90501
	14
	7.1
	72
	47

	90501
	15
	7.0
	-1
	42

	90501
	16
	7.0
	74
	38

	90501
	17
	6.7
	76
	37

	90501
	18
	7.4
	74
	39

	90501
	19
	7.6
	66
	54

	90501
	20
	7.4
	64
	61

	90501
	21
	7.2
	65
	66

	90501
	22
	7.1
	65
	63

	90501
	23
	7.0
	65
	62

	90501
	24
	6.8
	63
	68

	90502
	1
	6.9
	61
	72

	90502
	2
	6.9
	60
	72

	90502
	3
	6.6
	60
	71

	90502
	4
	6.9
	60
	71

	90502
	5
	6.7
	59
	72

	90502
	6
	6.7
	58
	76

	90502
	7
	6.6
	60
	74

	90502
	8
	6.5
	62
	71

	90502
	9
	6.5
	66
	65

	90502
	10
	6.6
	69
	61

	90502
	11
	6.7
	68
	63

	90502
	12
	6.7
	68
	62

	90502
	13
	6.6
	-1
	60

	90502
	14
	6.6
	68
	63

	90502
	15
	6.6
	68
	64

	90502
	16
	6.8
	68
	64

	90502
	17
	6.9
	68
	62

	90502
	18
	6.9
	66
	66

	90502
	19
	6.9
	63
	70

	90502
	20
	6.4
	61
	74

	90502
	21
	6.7
	60
	75

	90502
	22
	6.7
	60
	75

	90502
	23
	6.7
	60
	76

	90502
	24
	6.6
	59
	78

	90504
	1
	6.7
	60
	79

	90504
	2
	6.7
	60
	79

	90504
	3
	6.7
	60
	80

	90504
	4
	6.9
	60
	79

	90504
	5
	6.9
	61
	77

	90504
	6
	6.9
	61
	75

	90504
	7
	6.8
	63
	73

	90504
	8
	6.9
	65
	69

	90504
	9
	6.8
	68
	63

	90504
	10
	6.9
	71
	57

	90504
	11
	7.0
	74
	54

	90504
	12
	7.2
	74
	55

	90504
	13
	6.8
	75
	54

	90504
	14
	7.0
	75
	53

	90504
	15
	7.0
	74
	50

	90504
	16
	7.1
	74
	45

	90504
	17
	7.2
	73
	42

	90504
	18
	7.0
	71
	44

	90504
	19
	7.2
	68
	49

	90504
	20
	7.2
	66
	52

	90504
	21
	7.3
	64
	63

	90504
	22
	7.3
	62
	67

	90504
	23
	7.2
	61
	68

	90504
	24
	7.1
	61
	69

	90505
	1
	7.1
	60
	72

	90505
	2
	7.0
	58
	71

	90505
	3
	6.8
	57
	73

	90505
	4
	6.7
	57
	76

	90505
	5
	6.8
	56
	77

	90505
	6
	6.6
	56
	78

	90505
	7
	6.6
	62
	69

	90505
	8
	6.7
	66
	63

	90505
	9
	6.5
	68
	59

	90505
	10
	6.5
	71
	52

	90505
	11
	6.6
	74
	47

	90505
	12
	6.7
	77
	43

	90505
	13
	6.7
	79
	45

	90505
	14
	7.1
	78
	44

	90505
	15
	6.7
	-1
	43

	90505
	16
	6.7
	76
	41

	90505
	17
	6.7
	74
	49

	90505
	18
	6.7
	71
	57

	90505
	19
	6.8
	67
	63

	90505
	20
	7.5
	66
	66

	90505
	21
	7.6
	64
	72

	90505
	22
	7.2
	62
	78

	90505
	23
	6.8
	61
	79

	90505
	24
	6.7
	61
	79

	90507
	1
	7.6
	-1
	72

	90507
	2
	7.5
	-1
	72

	90507
	3
	7.6
	-1
	75

	90507
	4
	7.6
	-1
	-1

	90507
	5
	7.5
	-1
	-1

	90507
	6
	8.2
	-1
	75

	90507
	7
	8.5
	-1
	63

	90507
	8
	7.8
	-1
	57

	90507
	9
	7.7
	76
	49

	90507
	10
	7.3
	80
	45

	90507
	11
	7.3
	82
	40

	90507
	12
	7.6
	86
	35

	90507
	13
	7.5
	89
	32

	90507
	14
	7.8
	91
	29

	90507
	15
	8.2
	90
	29

	90507
	16
	8.2
	89
	25

	90507
	17
	8.5
	86
	27

	90507
	18
	8.7
	84
	30

	90507
	19
	8.8
	79
	38

	90507
	20
	8.7
	72
	52

	90507
	21
	8.7
	69
	61

	90507
	22
	8.1
	66
	64

	90507
	23
	8.1
	65
	65

	90507
	24
	8.2
	65
	66

	90508
	1
	8.0
	63
	68

	90508
	2
	7.6
	61
	70

	90508
	3
	7.3
	60
	72

	90508
	4
	7.0
	59
	74

	90508
	5
	7.8
	59
	76

	90508
	6
	8.0
	61
	74

	90508
	7
	7.9
	66
	63

	90508
	8
	7.4
	69
	60

	90508
	9
	7.3
	73
	56

	90508
	10
	7.2
	75
	53

	90508
	11
	7.6
	78
	49

	90508
	12
	7.8
	79
	46

	90508
	13
	7.8
	80
	44

	90508
	14
	7.7
	80
	43

	90508
	15
	7.0
	79
	44

	90508
	16
	7.1
	77
	46

	90508
	17
	7.3
	75
	51

	90508
	18
	7.9
	72
	57

	90508
	19
	8.1
	67
	66

	90508
	20
	8.2
	63
	73

	90508
	21
	8.1
	62
	76

	90508
	22
	8.0
	61
	77

	90508
	23
	7.8
	61
	78

	90508
	24
	7.9
	60
	79

	90509
	1
	7.8
	60
	81

	90509
	2
	7.8
	60
	81

	90509
	3
	7.7
	60
	82

	90509
	4
	7.6
	60
	82

	90509
	5
	7.9
	60
	82

	90509
	6
	7.8
	59
	83

	90509
	7
	7.8
	60
	82

	90509
	8
	7.6
	61
	80

	90509
	9
	7.5
	64
	74

	90509
	10
	7.0
	-1
	65

	90509
	11
	7.1
	72
	58

	90509
	12
	6.5
	76
	50

	90509
	13
	6.8
	76
	50

	90509
	14
	6.7
	75
	52

	90509
	15
	6.6
	75
	52

	90509
	16
	7.2
	75
	51

	90509
	17
	7.0
	74
	52

	90509
	18
	7.0
	72
	57

	90509
	19
	7.4
	68
	64

	90509
	20
	7.7
	-1
	71

	90509
	21
	7.5
	-1
	74

	90509
	22
	7.0
	61
	77

	90509
	23
	6.7
	60
	79

	90509
	24
	7.1
	59
	80

	90510
	1
	7.1
	60
	79

	90510
	2
	6.7
	60
	78

	90510
	3
	6.9
	61
	77

	90510
	4
	7.0
	60
	78

	90510
	5
	6.5
	60
	78

	90510
	6
	6.3
	61
	77

	90510
	7
	6.9
	61
	76

	90510
	8
	7.0
	62
	74

	90510
	9
	7.2
	63
	72

	90510
	10
	6.9
	65
	67

	90510
	11
	6.6
	68
	63

	90510
	12
	6.8
	72
	56

	90510
	13
	7.1
	74
	52

	90510
	14
	6.9
	75
	48

	90510
	15
	7.2
	77
	45

	90510
	16
	7.3
	76
	48

	90510
	17
	7.2
	75
	49

	90510
	18
	7.0
	73
	52

	90510
	19
	6.8
	69
	60

	90510
	20
	7.2
	64
	69

	90510
	21
	7.3
	61
	74

	90510
	22
	7.2
	60
	76

	90510
	23
	6.9
	59
	77

	90510
	24
	7.1
	-1
	78

	90512
	1
	7.3
	60
	78

	90512
	2
	6.8
	59
	80

	90512
	3
	7.0
	59
	79

	90512
	4
	7.0
	59
	79

	90512
	5
	7.2
	60
	78

	90512
	6
	7.0
	60
	77

	90512
	7
	6.6
	60
	81

	90512
	8
	7.2
	61
	76

	90512
	9
	7.2
	65
	67

	90512
	10
	7.2
	68
	59

	90512
	11
	7.1
	72
	52

	90512
	12
	6.7
	74
	48

	90512
	13
	6.6
	75
	50

	90512
	14
	7.1
	74
	50

	90512
	15
	7.6
	74
	51

	90512
	16
	7.8
	73
	51

	90512
	17
	7.8
	71
	55

	90512
	18
	7.8
	69
	58

	90512
	19
	7.9
	66
	62

	90512
	20
	8.0
	65
	63

	90512
	21
	7.9
	63
	66

	90512
	22
	8.0
	62
	69

	90512
	23
	8.0
	60
	71

	90512
	24
	8.0
	59
	73

	90513
	1
	12.8
	59
	76

	90513
	2
	6.9
	58
	79

	90513
	3
	6.3
	59
	78

	90513
	4
	7.0
	59
	79

	90513
	5
	7.6
	59
	78

	90513
	6
	7.7
	60
	76

	90513
	7
	7.5
	61
	74

	90513
	8
	7.5
	62
	72

	90513
	9
	7.0
	64
	70

	90513
	10
	6.5
	66
	66

	90513
	11
	6.3
	72
	55

	90513
	12
	6.7
	75
	49

	90513
	13
	7.2
	76
	48

	90513
	14
	7.1
	76
	48

	90513
	15
	7.3
	77
	48

	90513
	16
	7.2
	76
	49

	90513
	17
	7.3
	73
	52

	90513
	18
	7.4
	72
	53

	90513
	19
	7.8
	70
	55

	90513
	20
	7.8
	67
	60

	90513
	21
	7.6
	65
	63

	90513
	22
	7.2
	64
	68

	90513
	23
	7.2
	63
	73

	90513
	24
	7.0
	62
	75

	90514
	1
	6.9
	61
	76

	90514
	2
	7.0
	60
	78

	90514
	3
	6.9
	59
	80

	90514
	4
	6.9
	59
	82

	90514
	5
	6.9
	59
	83

	90514
	6
	6.9
	58
	84

	90514
	7
	6.8
	61
	79

	90514
	8
	6.8
	64
	73

	90514
	9
	6.6
	68
	65

	90514
	10
	6.8
	72
	57

	90514
	11
	7.1
	75
	52

	90514
	12
	7.0
	78
	49

	90514
	13
	7.1
	78
	48

	90514
	14
	6.9
	80
	46

	90514
	15
	7.0
	79
	47

	90514
	16
	7.1
	77
	49

	90514
	17
	7.4
	75
	52

	90514
	18
	7.5
	72
	57

	90514
	19
	7.4
	68
	66

	90514
	20
	7.3
	65
	71

	90514
	21
	7.2
	63
	74

	90514
	22
	7.2
	62
	74

	90514
	23
	7.2
	62
	76

	90514
	24
	7.1
	61
	77

	90516
	1
	6.8
	61
	78

	90516
	2
	6.7
	60
	78

	90516
	3
	7.2
	59
	80

	90516
	4
	7.0
	58
	81

	90516
	5
	7.0
	58
	81

	90516
	6
	7.0
	59
	80

	90516
	7
	7.0
	64
	74

	90516
	8
	6.8
	67
	68

	90516
	9
	6.7
	71
	62

	90516
	10
	6.8
	74
	57

	90516
	11
	6.9
	78
	51

	90516
	12
	7.0
	81
	48

	90516
	13
	7.0
	81
	49

	90516
	14
	7.1
	79
	51

	90516
	15
	6.9
	78
	52

	90516
	16
	7.2
	76
	54

	90516
	17
	7.5
	73
	59

	90516
	18
	7.4
	70
	64

	90516
	19
	7.2
	67
	69

	90516
	20
	7.2
	64
	74

	90516
	21
	7.4
	64
	76

	90516
	22
	7.1
	64
	76

	90516
	23
	7.1
	63
	76

	90516
	24
	7.2
	63
	78

	90517
	1
	7.0
	62
	79

	90517
	2
	7.2
	62
	78

	90517
	3
	7.1
	62
	78

	90517
	4
	6.7
	61
	82

	90517
	5
	6.8
	61
	84

	90517
	6
	6.8
	61
	83

	90517
	7
	6.7
	62
	81

	90517
	8
	6.8
	64
	78

	90517
	9
	7.1
	66
	74

	90517
	10
	6.9
	69
	68

	90517
	11
	6.9
	73
	60

	90517
	12
	6.8
	78
	52

	90517
	13
	6.7
	81
	49

	90517
	14
	6.9
	83
	46

	90517
	15
	6.9
	84
	45

	90517
	16
	6.7
	81
	48

	90517
	17
	6.7
	78
	52

	90517
	18
	6.9
	76
	53

	90517
	19
	7.2
	72
	59

	90517
	20
	7.1
	67
	69

	90517
	21
	7.1
	65
	75

	90517
	22
	7.0
	63
	78

	90517
	23
	7.1
	62
	80

	90517
	24
	6.9
	62
	81

	90518
	1
	7.1
	62
	81

	90518
	2
	6.6
	62
	81

	90518
	3
	6.6
	62
	81

	90518
	4
	6.6
	62
	80

	90518
	5
	6.5
	62
	80

	90518
	6
	6.5
	63
	79

	90518
	7
	6.8
	64
	77

	90518
	8
	6.8
	67
	71

	90518
	9
	6.5
	71
	64

	90518
	10
	6.7
	75
	57

	90518
	11
	6.6
	79
	50

	90518
	12
	6.7
	82
	45

	90518
	13
	6.8
	83
	44

	90518
	14
	6.9
	79
	49

	90518
	15
	6.7
	80
	46

	90518
	16
	6.8
	79
	46

	90518
	17
	6.9
	76
	50

	90518
	18
	6.9
	71
	56

	90518
	19
	7.1
	66
	65

	90518
	20
	7.2
	63
	71

	90518
	21
	7.1
	62
	76

	90518
	22
	6.9
	60
	79

	90518
	23
	7.0
	60
	80

	90518
	24
	7.0
	59
	80

	90519
	1
	7.1
	59
	80

	90519
	2
	7.2
	59
	80

	90519
	3
	7.0
	60
	78

	90519
	4
	7.1
	60
	79

	90519
	5
	7.1
	59
	80

	90519
	6
	7.0
	60
	79

	90519
	7
	7.2
	64
	72

	90519
	8
	7.0
	66
	68

	90519
	9
	6.8
	69
	62

	90519
	10
	7.1
	73
	56

	90519
	11
	7.2
	76
	50

	90519
	12
	7.3
	78
	46

	90519
	13
	7.0
	80
	42

	90519
	14
	7.0
	80
	38

	90519
	15
	7.2
	80
	38

	90519
	16
	7.0
	78
	42

	90519
	17
	7.2
	75
	48

	90519
	18
	7.4
	70
	56

	90519
	19
	7.6
	67
	63

	90519
	20
	7.7
	65
	65

	90519
	21
	7.5
	64
	67

	90519
	22
	7.5
	62
	71

	90519
	23
	7.2
	62
	73

	90519
	24
	7.3
	62
	74

	90521
	1
	7.1
	61
	78

	90521
	2
	7.2
	60
	81

	90521
	3
	7.0
	60
	81

	90521
	4
	7.0
	60
	80

	90521
	5
	6.9
	61
	78

	90521
	6
	6.7
	61
	76

	90521
	7
	6.9
	62
	75

	90521
	8
	7.1
	66
	67

	90521
	9
	7.5
	69
	60

	90521
	10
	7.5
	71
	55

	90521
	11
	7.3
	74
	50

	90521
	12
	7.4
	76
	46

	90521
	13
	7.3
	76
	45

	90521
	14
	7.4
	78
	41

	90521
	15
	7.5
	78
	39

	90521
	16
	7.7
	78
	41

	90521
	17
	7.7
	75
	49

	90521
	18
	7.5
	72
	55

	90521
	19
	7.6
	68
	61

	90521
	20
	7.5
	66
	66

	90521
	21
	7.5
	64
	71

	90521
	22
	7.2
	63
	75

	90521
	23
	7.2
	62
	75

	90521
	24
	7.1
	61
	75

	90522
	1
	7.2
	62
	75

	90522
	2
	6.8
	62
	75

	90522
	3
	7.1
	61
	75

	90522
	4
	7.2
	61
	74

	90522
	5
	7.2
	61
	74

	90522
	6
	7.3
	61
	72

	90522
	7
	7.5
	62
	69

	90522
	8
	7.4
	65
	64

	90522
	9
	7.4
	69
	60

	90522
	10
	7.5
	71
	55

	90522
	11
	7.4
	73
	51

	90522
	12
	7.6
	73
	49

	90522
	13
	7.5
	75
	45

	90522
	14
	7.6
	76
	45

	90522
	15
	7.4
	76
	46

	90522
	16
	7.3
	75
	46

	90522
	17
	7.4
	74
	48

	90522
	18
	7.3
	69
	55

	90522
	19
	7.4
	65
	62

	90522
	20
	7.3
	63
	67

	90522
	21
	7.3
	62
	70

	90522
	22
	7.2
	61
	72

	90522
	23
	6.9
	60
	74

	90522
	24
	7.2
	60
	74

	90523
	1
	7.3
	60
	73

	90523
	2
	7.2
	60
	72

	90523
	3
	7.1
	60
	72

	90523
	4
	7.1
	60
	72

	90523
	5
	7.3
	60
	72

	90523
	6
	7.3
	60
	70

	90523
	7
	7.2
	61
	69

	90523
	8
	7.2
	63
	66

	90523
	9
	7.1
	66
	61

	90523
	10
	7.0
	68
	57

	90523
	11
	6.9
	71
	51

	90523
	12
	6.9
	74
	43

	90523
	13
	6.5
	76
	43

	90523
	14
	6.9
	76
	43

	90523
	15
	7.2
	76
	42

	90523
	16
	7.2
	73
	46

	90523
	17
	7.3
	72
	48

	90523
	18
	7.3
	70
	51

	90523
	19
	7.3
	65
	59

	90523
	20
	7.4
	62
	64

	90523
	21
	7.4
	61
	67

	90523
	22
	7.2
	60
	69

	90523
	23
	7.1
	59
	71

	90523
	24
	7.0
	58
	73

	90524
	1
	5.3
	59
	72

	90524
	2
	6.9
	60
	70

	90524
	3
	7.1
	60
	69

	90524
	4
	7.0
	60
	67

	90524
	5
	6.9
	59
	66

	90524
	6
	7.0
	59
	66

	90524
	7
	7.5
	61
	64

	90524
	11
	0.0
	70
	49

	90524
	12
	0.0
	72
	46

	90524
	13
	0.0
	75
	40

	90524
	14
	0.0
	75
	42

	90524
	16
	0.0
	72
	47

	90524
	17
	0.0
	70
	54

	90524
	21
	0.0
	61
	72

	90524
	22
	0.0
	60
	73

	90524
	23
	0.0
	60
	73

	90527
	7
	0.1
	62
	72

	90528
	7
	13.5
	63
	71

	90528
	8
	18.9
	64
	70

	90528
	9
	13.1
	66
	67

	90528
	10
	14.7
	69
	61

	90528
	11
	15.3
	73
	55

	90528
	12
	16.7
	74
	53

	90529
	1
	6.8
	63
	71

	90529
	7
	19.3
	62
	74

	90529
	8
	20.0
	62
	74

	90529
	9
	20.0
	62
	76

	90529
	10
	11.3
	63
	73

	90529
	11
	7.3
	65
	69

	90529
	12
	6.5
	66
	68

	90529
	13
	6.4
	67
	66

	90529
	14
	6.5
	66
	68

	90529
	15
	6.1
	65
	69

	90529
	16
	6.0
	65
	69

	90529
	17
	6.2
	64
	69

	90529
	18
	6.7
	64
	70

	90529
	19
	7.5
	63
	71

	90529
	20
	7.1
	62
	74

	90529
	21
	6.4
	61
	75

	90529
	22
	6.7
	61
	76

	90529
	23
	6.7
	61
	77

	90529
	24
	6.8
	61
	76

	90530
	1
	6.7
	61
	77

	90530
	2
	6.8
	61
	77

	90530
	3
	6.9
	60
	77

	90530
	4
	7.0
	60
	77

	90530
	5
	7.1
	60
	78

	90530
	6
	7.1
	59
	80

	90530
	7
	7.1
	60
	79

	90530
	8
	7.1
	60
	77

	90530
	9
	7.1
	62
	75

	90530
	10
	7.1
	63
	71

	90530
	11
	7.1
	65
	67

	90530
	12
	7.2
	67
	64

	90530
	13
	7.2
	67
	63

	90530
	14
	7.2
	-1
	64

	90530
	15
	6.9
	67
	64

	90530
	16
	6.8
	67
	64

	90530
	17
	6.7
	67
	64

	90530
	18
	6.6
	65
	67

	90530
	19
	6.6
	63
	71

	90530
	20
	6.8
	61
	73

	90530
	21
	6.8
	61
	73

	90530
	22
	6.7
	61
	73

	90530
	23
	6.6
	61
	73

	90530
	24
	6.8
	61
	73

	90602
	1
	6.8
	63
	72

	90602
	2
	6.7
	63
	73

	90602
	3
	6.7
	62
	76

	90602
	4
	6.6
	62
	76

	90602
	5
	6.6
	61
	78

	90602
	6
	6.7
	61
	78

	90602
	7
	6.6
	61
	77

	90602
	8
	5.9
	63
	75

	90602
	9
	6.3
	64
	71

	90602
	10
	6.8
	67
	64

	90602
	11
	6.2
	71
	58

	90602
	12
	5.5
	75
	52

	90602
	13
	6.0
	77
	46

	90602
	14
	6.5
	80
	38

	90602
	15
	6.4
	81
	35

	90602
	16
	6.3
	80
	40

	90602
	17
	6.5
	78
	43

	90602
	18
	6.6
	75
	50

	90602
	19
	6.6
	69
	59

	90602
	20
	6.6
	65
	69

	90602
	21
	6.7
	63
	72

	90602
	22
	6.8
	62
	73

	90602
	23
	6.7
	61
	75

	90602
	24
	6.6
	60
	78

	90603
	1
	6.5
	59
	80

	90603
	2
	6.7
	60
	79

	90603
	3
	6.5
	60
	79

	90603
	4
	6.6
	60
	78

	90603
	5
	6.6
	60
	78

	90603
	6
	6.6
	61
	77

	90603
	7
	6.5
	63
	74

	90603
	8
	6.5
	66
	69

	90603
	9
	6.6
	68
	65

	90603
	10
	6.6
	70
	62

	90603
	11
	6.5
	68
	63

	90603
	12
	6.6
	67
	64

	90603
	13
	6.8
	67
	65

	90603
	14
	6.8
	66
	68

	90603
	15
	6.8
	64
	74

	90603
	16
	6.9
	62
	77

	90603
	17
	7.0
	62
	77

	90603
	18
	6.9
	62
	77

	90603
	19
	6.6
	62
	75

	90603
	20
	6.5
	61
	77

	90603
	21
	6.8
	61
	77

	90603
	22
	6.7
	61
	77

	90603
	23
	6.6
	60
	78

	90603
	24
	6.6
	60
	78

	90605
	1
	6.5
	61
	75

	90605
	2
	6.7
	60
	76

	90605
	3
	6.7
	60
	78

	90605
	4
	6.6
	60
	78

	90605
	5
	6.8
	60
	79

	90605
	6
	7.0
	60
	78

	90605
	7
	6.9
	62
	74

	90605
	8
	6.6
	61
	74

	90605
	9
	6.5
	63
	70

	90605
	10
	6.6
	63
	70

	90605
	11
	6.8
	65
	65

	90605
	12
	6.6
	65
	60

	90605
	13
	6.2
	65
	62

	90605
	14
	6.1
	67
	58

	90605
	15
	6.7
	66
	63

	90605
	16
	6.6
	67
	58

	90605
	17
	6.9
	69
	56

	90605
	18
	6.7
	67
	57

	90605
	19
	6.6
	64
	62

	90605
	20
	6.9
	62
	67

	90605
	21
	6.7
	61
	69

	90605
	22
	6.7
	60
	71

	90605
	23
	6.7
	-1
	75

	90605
	24
	6.4
	57
	77

	90606
	1
	6.8
	57
	78

	90606
	2
	6.8
	56
	80

	90606
	3
	6.9
	57
	80

	90606
	4
	6.9
	57
	80

	90606
	5
	7.0
	56
	80

	90606
	6
	6.8
	57
	78

	90606
	7
	6.5
	61
	70

	90606
	8
	6.3
	65
	65

	90606
	9
	6.2
	68
	56

	90606
	10
	6.1
	66
	56

	90606
	11
	6.3
	67
	56

	90606
	12
	6.6
	71
	48

	90606
	13
	6.8
	69
	52

	90606
	14
	6.8
	71
	48

	90606
	15
	6.8
	71
	49

	90606
	16
	7.1
	69
	54

	90606
	17
	7.1
	68
	56

	90606
	18
	7.2
	66
	58

	90606
	19
	7.4
	64
	63

	90606
	20
	7.4
	63
	70

	90606
	21
	7.0
	62
	70

	90606
	22
	6.8
	62
	71

	90606
	23
	6.6
	61
	73

	90606
	24
	6.8
	61
	72

	90607
	1
	6.8
	61
	73

	90607
	2
	6.6
	61
	72

	90607
	3
	6.7
	60
	74

	90607
	4
	6.7
	59
	76

	90607
	5
	6.7
	58
	77

	90607
	6
	6.6
	59
	74

	90607
	7
	6.8
	62
	68

	90607
	8
	6.8
	65
	64

	90607
	9
	6.7
	67
	56

	90607
	10
	6.8
	68
	53

	90607
	11
	6.9
	69
	52

	90607
	12
	6.8
	70
	52

	90607
	13
	7.0
	72
	50

	90607
	14
	6.9
	73
	48

	90607
	15
	6.8
	72
	50

	90607
	16
	6.7
	71
	52

	90607
	17
	6.7
	70
	53

	90607
	18
	7.0
	69
	54

	90607
	19
	7.3
	66
	59

	90607
	20
	7.3
	64
	64

	90607
	21
	7.3
	62
	68

	90607
	22
	7.2
	61
	73

	90607
	23
	7.1
	60
	75

	90607
	24
	7.3
	59
	77

	90608
	1
	7.0
	59
	78

	90608
	2
	6.8
	57
	79

	90608
	3
	6.8
	57
	80

	90608
	4
	6.9
	56
	80

	90608
	5
	6.8
	57
	81

	90608
	6
	6.9
	58
	80

	90608
	7
	6.8
	61
	75

	90608
	8
	6.8
	62
	71

	90608
	9
	6.6
	65
	64

	90608
	10
	6.8
	66
	61

	90608
	11
	6.6
	67
	59

	90608
	12
	7.0
	70
	53

	90608
	13
	6.3
	70
	53

	90608
	14
	6.2
	70
	53

	90608
	15
	6.2
	72
	50

	90608
	16
	6.4
	71
	52

	90608
	17
	6.6
	70
	52

	90608
	18
	6.6
	69
	53

	90608
	19
	6.1
	66
	59

	90608
	20
	6.1
	63
	64

	90608
	21
	6.3
	62
	66

	90608
	22
	6.4
	60
	69

	90608
	23
	6.4
	59
	75

	90608
	24
	6.8
	59
	78

	90609
	1
	6.4
	60
	77

	90609
	2
	6.4
	61
	74

	90609
	3
	6.2
	61
	72

	90609
	4
	6.0
	61
	72

	90609
	5
	6.5
	61
	69

	90609
	6
	6.4
	61
	69

	90609
	7
	6.9
	61
	69

	90609
	8
	6.7
	62
	67

	90609
	9
	6.8
	62
	69

	90609
	10
	6.3
	63
	68

	90609
	11
	6.8
	64
	65

	90609
	12
	6.8
	65
	62

	90609
	13
	6.4
	69
	53

	90609
	14
	6.8
	70
	50

	90609
	15
	7.6
	69
	53

	90609
	16
	5.2
	68
	59

	90609
	17
	6.3
	68
	58

	90609
	18
	6.1
	68
	58

	90609
	19
	6.2
	65
	61

	90609
	20
	6.2
	64
	63

	90609
	21
	6.3
	63
	66

	90609
	22
	6.7
	61
	71

	90609
	23
	6.5
	60
	73

	90609
	24
	6.0
	59
	75

	90611
	1
	7.4
	61
	71

	90611
	2
	7.3
	61
	71

	90611
	3
	7.4
	61
	71

	90611
	4
	7.7
	61
	71

	90611
	5
	7.4
	61
	72

	90611
	6
	7.3
	61
	72

	90611
	7
	7.3
	62
	71

	90611
	8
	7.4
	63
	66

	90611
	9
	7.1
	64
	63

	90611
	10
	6.5
	64
	66

	90611
	11
	6.4
	63
	70

	90611
	12
	7.0
	64
	66

	90611
	13
	6.9
	67
	61

	90611
	14
	6.5
	69
	58

	90611
	15
	6.8
	69
	57

	90611
	16
	6.7
	70
	56

	90611
	17
	6.7
	71
	53

	90611
	18
	6.6
	70
	55

	90611
	19
	7.2
	66
	61

	90611
	20
	7.7
	65
	64

	90611
	21
	7.8
	64
	67

	90611
	22
	7.6
	63
	69

	90611
	23
	7.7
	63
	69

	90611
	24
	7.6
	63
	70

	90612
	1
	7.5
	63
	72

	90612
	2
	8.1
	62
	74

	90612
	3
	14.1
	61
	76

	90612
	4
	8.2
	61
	74

	90612
	5
	7.4
	61
	73

	90612
	6
	7.7
	62
	71

	90612
	7
	7.7
	63
	70

	90612
	8
	6.8
	64
	69

	90612
	9
	6.8
	63
	71

	90612
	10
	6.9
	64
	69

	90612
	11
	6.8
	-1
	64

	90612
	12
	6.9
	66
	64

	90612
	13
	6.8
	67
	63

	90612
	14
	6.6
	68
	61

	90612
	15
	6.9
	68
	59

	90612
	16
	6.4
	68
	57

	90612
	17
	6.2
	68
	58

	90612
	18
	6.4
	67
	59

	90612
	19
	6.6
	66
	60

	90612
	20
	6.5
	65
	63

	90612
	21
	6.6
	64
	67

	90612
	22
	6.5
	63
	70

	90612
	23
	6.5
	63
	73

	90612
	24
	6.5
	62
	74

	90616
	1
	7.1
	62
	76

	90616
	2
	7.0
	63
	76

	90616
	3
	7.0
	63
	75

	90616
	4
	7.2
	62
	75

	90616
	5
	7.3
	62
	76

	90616
	6
	7.6
	63
	74

	90616
	7
	7.7
	65
	69

	90616
	8
	6.8
	67
	65

	90616
	9
	5.8
	71
	57

	90616
	10
	7.0
	73
	51

	90616
	11
	6.6
	74
	51

	90616
	12
	7.1
	75
	48

	90616
	13
	7.3
	77
	46

	90616
	14
	7.2
	78
	46

	90616
	15
	7.3
	77
	48

	90616
	16
	7.0
	76
	46

	90616
	17
	7.1
	75
	48

	90616
	18
	7.1
	72
	54

	90616
	19
	7.1
	70
	57

	90616
	20
	7.4
	67
	61

	90616
	21
	7.5
	66
	65

	90616
	22
	7.6
	65
	68

	90616
	23
	7.5
	64
	71

	90616
	24
	7.6
	63
	75

	90618
	1
	6.6
	62
	76

	90618
	2
	6.4
	62
	79

	90618
	3
	6.9
	61
	80

	90618
	4
	6.6
	61
	80

	90618
	5
	6.5
	61
	79

	90618
	6
	6.7
	63
	77

	90618
	7
	6.5
	63
	75

	90618
	8
	7.3
	65
	72

	90618
	9
	7.7
	70
	64

	90618
	10
	7.5
	73
	58

	90618
	11
	7.2
	76
	54

	90618
	12
	6.8
	78
	50

	90618
	13
	7.1
	81
	47

	90618
	14
	7.0
	81
	48

	90618
	15
	6.3
	80
	48

	90618
	16
	5.8
	79
	49

	90618
	17
	5.8
	78
	51

	90618
	18
	6.3
	76
	54

	90618
	19
	6.6
	72
	60

	90618
	20
	6.8
	69
	67

	90618
	21
	7.1
	67
	72

	90618
	22
	7.4
	65
	74

	90618
	23
	7.1
	65
	74

	90618
	24
	7.3
	64
	75

	90619
	1
	7.6
	64
	75

	90619
	2
	7.1
	63
	77

	90619
	3
	7.3
	63
	78

	90619
	4
	7.4
	62
	79

	90619
	5
	6.9
	63
	81

	90619
	6
	7.1
	64
	80

	90619
	7
	7.1
	65
	77

	90619
	8
	6.7
	68
	71

	90619
	9
	7.3
	72
	64

	90619
	10
	7.3
	74
	61

	90619
	11
	7.0
	77
	55

	90619
	12
	7.1
	79
	53

	90619
	13
	6.9
	81
	51

	90619
	14
	6.9
	82
	49

	90619
	15
	6.6
	80
	52

	90619
	16
	6.2
	78
	54

	90619
	17
	6.0
	77
	55

	90619
	18
	5.9
	73
	61

	90619
	19
	6.3
	68
	70

	90619
	20
	7.2
	65
	74

	90619
	21
	8.0
	65
	75

	90619
	22
	7.8
	64
	75

	90619
	23
	8.0
	65
	75

	90619
	24
	8.1
	64
	77

	90621
	1
	7.5
	64
	68

	90621
	2
	7.4
	64
	71

	90621
	3
	8.4
	63
	69

	90621
	4
	8.4
	63
	68

	90621
	5
	8.1
	63
	67

	90621
	6
	7.9
	64
	66

	90621
	7
	7.3
	68
	61

	90621
	8
	7.1
	68
	60

	90621
	9
	6.8
	69
	56

	90621
	10
	7.2
	72
	51

	90621
	11
	7.4
	75
	46

	90621
	12
	7.6
	75
	45

	90621
	13
	7.4
	76
	45

	90621
	14
	7.4
	76
	45

	90621
	15
	7.2
	76
	47

	90621
	16
	7.1
	74
	49

	90621
	17
	7.4
	-1
	49

	90621
	18
	7.4
	-1
	50

	90621
	19
	7.6
	-1
	53

	90621
	20
	7.7
	-1
	57

	90621
	21
	8.0
	-1
	58

	90621
	22
	8.0
	62
	65

	90621
	23
	7.6
	62
	66

	90621
	24
	7.3
	60
	67

	90622
	1
	7.6
	58
	66

	90622
	2
	7.4
	57
	68

	90622
	3
	7.5
	56
	69

	90622
	4
	7.7
	55
	72

	90622
	5
	7.8
	55
	73

	90622
	6
	7.9
	58
	69

	90622
	7
	7.8
	65
	62

	90622
	8
	7.6
	66
	62

	90622
	9
	7.3
	69
	58

	90622
	10
	7.0
	71
	56

	90622
	11
	7.2
	75
	50

	90622
	12
	7.3
	77
	46

	90622
	13
	7.3
	78
	46

	90622
	14
	7.5
	78
	47

	90622
	15
	7.5
	78
	46

	90622
	16
	7.3
	77
	47

	90622
	17
	7.3
	76
	49

	90622
	18
	7.3
	73
	54

	90622
	19
	7.5
	70
	58

	90622
	20
	7.8
	67
	62

	90622
	21
	7.6
	65
	66

	90622
	22
	7.7
	64
	68

	90622
	23
	7.6
	63
	71

	90622
	24
	7.5
	62
	74

	90625
	1
	7.0
	61
	77

	90625
	2
	7.1
	60
	78

	90625
	3
	7.0
	61
	77

	90625
	4
	7.1
	61
	77

	90625
	5
	7.1
	61
	77

	90625
	6
	7.2
	61
	77

	90625
	7
	7.0
	62
	75

	90625
	8
	7.0
	63
	72

	90625
	9
	6.9
	66
	67

	90625
	10
	6.8
	70
	61

	90625
	11
	6.5
	73
	56

	90625
	12
	6.4
	75
	52

	90625
	13
	6.4
	78
	48

	90625
	14
	6.3
	76
	50

	90625
	15
	6.5
	75
	52

	90625
	16
	6.6
	74
	53

	90625
	17
	6.8
	72
	56

	90625
	18
	6.5
	70
	60

	90625
	19
	6.7
	67
	66

	90625
	20
	6.7
	64
	72

	90625
	21
	6.9
	62
	75

	90625
	22
	7.2
	62
	77

	90625
	23
	6.9
	61
	78

	90625
	24
	6.8
	60
	79

	90626
	1
	7.0
	59
	80

	90626
	2
	6.6
	58
	81

	90626
	3
	6.7
	58
	82

	90626
	16
	6.7
	81
	41

	90626
	17
	6.9
	80
	41

	90626
	18
	7.3
	77
	44

	90626
	19
	7.4
	74
	50

	90626
	20
	7.6
	70
	60

	90626
	21
	8.0
	67
	67

	90626
	22
	8.2
	65
	73

	90626
	23
	7.9
	63
	75

	90626
	24
	7.7
	63
	76

	90627
	1
	8.0
	63
	77

	90627
	2
	8.1
	62
	77

	90627
	3
	8.1
	62
	77

	90627
	4
	7.5
	61
	79

	90627
	5
	7.7
	61
	82

	90627
	6
	8.1
	61
	81

	90627
	7
	7.7
	66
	73

	90627
	8
	7.5
	68
	70

	90627
	9
	7.7
	72
	62

	90627
	10
	7.7
	76
	55

	90627
	11
	7.6
	80
	47

	90627
	12
	7.4
	84
	41

	90627
	13
	7.4
	86
	39

	90627
	14
	7.5
	87
	40

	90627
	15
	7.7
	86
	39

	90627
	16
	7.5
	85
	40

	90627
	17
	7.5
	-1
	44

	90627
	18
	7.5
	80
	46

	90627
	19
	7.6
	76
	52

	90627
	20
	7.9
	72
	60

	90627
	21
	7.8
	69
	68

	90627
	22
	7.8
	66
	71

	90627
	23
	7.5
	65
	74

	90627
	24
	7.4
	64
	75

	90630
	1
	7.7
	63
	77

	90630
	2
	7.9
	61
	80

	90630
	3
	8.0
	61
	81

	90630
	4
	7.8
	60
	81

	90630
	5
	8.0
	60
	81

	90630
	6
	8.0
	61
	80

	90630
	7
	8.1
	64
	76

	90630
	8
	7.9
	67
	70

	90630
	9
	7.8
	71
	63

	90630
	10
	7.8
	74
	57

	90630
	11
	7.6
	77
	52

	90630
	12
	7.8
	79
	49

	90630
	13
	7.7
	79
	48

	90630
	14
	7.6
	79
	47

	90630
	15
	7.8
	80
	44

	90630
	16
	7.7
	79
	42

	90630
	17
	7.5
	77
	46

	90630
	18
	7.4
	75
	48

	90630
	19
	7.4
	70
	57

	90630
	20
	7.9
	66
	67

	90630
	21
	8.2
	64
	73

	90630
	22
	8.1
	63
	75

	90630
	23
	7.4
	62
	76

	90630
	24
	7.6
	62
	77

	90701
	1
	6.7
	62
	77

	90701
	2
	6.6
	61
	78

	90701
	3
	6.7
	62
	78

	90701
	18
	21.5
	76
	52

	90701
	19
	7.1
	72
	56

	90701
	20
	9.0
	68
	61

	90701
	22
	12.7
	65
	69

	90701
	23
	5.8
	64
	71

	90701
	24
	6.3
	63
	74

	90704
	1
	7.8
	62
	75

	90704
	2
	7.8
	60
	76

	90704
	3
	7.5
	59
	77

	90704
	4
	7.1
	59
	78

	90704
	5
	7.1
	58
	79

	90704
	6
	7.0
	61
	76

	90704
	7
	7.1
	66
	68

	90704
	8
	7.2
	68
	65

	90704
	9
	7.0
	71
	60

	90704
	10
	6.8
	75
	53

	90704
	11
	6.9
	78
	48

	90704
	12
	7.0
	82
	40

	90704
	13
	7.0
	85
	35

	90704
	14
	7.4
	86
	30

	90704
	15
	7.5
	84
	33

	90704
	16
	7.3
	79
	40

	90704
	17
	7.2
	77
	43

	90704
	18
	7.4
	75
	48

	90704
	19
	7.7
	71
	54

	90704
	20
	7.4
	67
	59

	90704
	21
	7.6
	65
	62

	90704
	22
	7.6
	64
	63

	90704
	23
	7.4
	64
	64

	90704
	24
	7.3
	63
	67

	90705
	1
	7.5
	62
	71

	90705
	2
	7.6
	61
	73

	90705
	3
	7.6
	61
	73

	90705
	4
	7.2
	60
	75

	90705
	5
	7.1
	59
	77

	90705
	6
	7.0
	62
	72

	90705
	7
	7.2
	67
	64

	90705
	8
	7.0
	70
	58

	90705
	9
	7.2
	73
	53

	90705
	10
	6.8
	76
	47

	90705
	11
	7.1
	79
	41

	90705
	12
	7.4
	81
	41

	90705
	13
	7.5
	82
	40

	90705
	14
	7.6
	81
	40

	90705
	15
	7.7
	80
	42

	90705
	16
	7.6
	78
	43

	90705
	17
	7.7
	77
	46

	90705
	18
	7.7
	74
	49

	90705
	19
	7.9
	71
	54

	90705
	20
	7.9
	67
	60

	90705
	21
	7.9
	65
	64

	90705
	22
	7.9
	64
	67

	90705
	23
	7.7
	63
	70

	90705
	24
	7.8
	61
	72

	90707
	1
	7.5
	64
	74

	90707
	2
	7.5
	63
	78

	90707
	3
	7.4
	62
	79

	90707
	4
	7.3
	62
	81

	90707
	5
	7.6
	62
	80

	90707
	6
	8.2
	63
	79

	90707
	7
	7.7
	66
	73

	90707
	8
	7.4
	68
	68

	90707
	9
	7.6
	70
	64

	90707
	10
	7.3
	74
	59

	90707
	11
	7.6
	77
	53

	90707
	12
	7.0
	79
	51

	90707
	13
	7.2
	79
	46

	90707
	14
	7.1
	80
	45

	90707
	15
	7.5
	79
	46

	90707
	16
	7.4
	80
	42

	90707
	17
	6.8
	79
	46

	90707
	18
	7.0
	78
	50

	90707
	19
	7.2
	74
	58

	90707
	20
	7.1
	69
	66

	90707
	21
	6.8
	66
	71

	90707
	22
	7.6
	65
	74

	90707
	23
	7.7
	64
	77

	90707
	24
	6.9
	63
	79

	90708
	1
	7.3
	63
	80

	90708
	2
	6.7
	62
	81

	90708
	3
	7.2
	62
	82

	90708
	4
	7.4
	62
	82

	90708
	5
	6.5
	63
	78

	90708
	6
	6.9
	63
	77

	90708
	7
	6.2
	64
	76

	90708
	8
	6.3
	66
	71

	90708
	9
	5.9
	70
	64

	90708
	10
	5.6
	74
	57

	90708
	11
	6.1
	77
	51

	90708
	12
	5.9
	80
	46

	90708
	13
	6.1
	83
	41

	90708
	14
	6.9
	86
	34

	90708
	15
	6.4
	85
	36

	90708
	16
	6.4
	82
	42

	90708
	17
	6.0
	78
	49

	90708
	18
	6.8
	74
	55

	90708
	19
	5.8
	71
	59

	90708
	20
	6.1
	68
	66

	90708
	21
	6.3
	66
	70

	90708
	22
	6.5
	65
	72

	90708
	23
	7.0
	64
	75

	90708
	24
	7.3
	63
	77

	90710
	1
	7.4
	63
	74

	90710
	2
	7.3
	61
	76

	90710
	3
	7.4
	60
	77

	90710
	4
	7.3
	60
	79

	90710
	5
	7.1
	59
	79

	90710
	6
	7.3
	63
	75

	90710
	7
	7.0
	68
	67

	90710
	8
	7.2
	70
	63

	90710
	9
	7.1
	74
	57

	90710
	10
	7.0
	77
	51

	90710
	11
	6.9
	82
	39

	90710
	12
	7.2
	87
	25

	90710
	13
	7.1
	91
	19

	90710
	14
	6.9
	91
	23

	90710
	15
	6.9
	88
	36

	90710
	16
	7.5
	85
	37

	90710
	17
	7.3
	83
	37

	90710
	18
	7.4
	82
	34

	90710
	19
	7.3
	79
	35

	90710
	20
	7.8
	74
	42

	90710
	21
	7.5
	72
	49

	90710
	22
	7.4
	70
	51

	90710
	23
	7.2
	69
	56

	90710
	24
	7.6
	68
	61

	90713
	1
	7.1
	67
	60

	90713
	2
	6.7
	66
	60

	90713
	3
	6.4
	65
	61

	90713
	4
	7.1
	65
	62

	90713
	5
	7.3
	65
	66

	90713
	6
	7.3
	67
	65

	90713
	7
	7.3
	71
	63

	90713
	8
	6.5
	75
	57

	90713
	9
	6.7
	81
	47

	90713
	10
	7.0
	84
	39

	90713
	11
	7.3
	88
	31

	90713
	12
	7.2
	91
	27

	90713
	13
	7.0
	93
	28

	90713
	14
	7.2
	93
	30

	90713
	15
	7.4
	91
	31

	90713
	16
	6.9
	90
	29

	90713
	17
	7.4
	88
	26

	90713
	18
	8.0
	85
	24

	90713
	19
	7.9
	79
	37

	90713
	20
	7.6
	75
	44

	90713
	21
	7.7
	72
	51

	90713
	22
	7.6
	69
	56

	90713
	23
	7.6
	68
	59

	90713
	24
	7.3
	68
	62

	90714
	1
	7.2
	67
	67

	90714
	2
	7.2
	67
	71

	90714
	3
	7.1
	65
	72

	90714
	4
	7.1
	64
	73

	90714
	5
	7.3
	64
	73

	90714
	6
	6.9
	66
	70

	90714
	7
	7.1
	70
	69

	90714
	8
	7.0
	72
	65

	90714
	9
	7.2
	76
	56

	90714
	10
	7.2
	80
	48

	90714
	11
	7.4
	84
	40

	90714
	12
	7.6
	86
	35

	90714
	13
	7.7
	89
	38

	90714
	14
	7.5
	89
	37

	90714
	15
	7.5
	89
	31

	90714
	16
	7.0
	88
	36

	90714
	17
	6.9
	84
	41

	90714
	18
	7.5
	81
	46

	90714
	19
	7.8
	76
	52

	90714
	20
	7.5
	72
	59

	90714
	21
	7.2
	70
	64

	90714
	22
	7.3
	69
	67

	90714
	23
	7.4
	67
	71

	90714
	24
	7.4
	66
	75

	90716
	1
	7.3
	65
	75

	90716
	2
	7.1
	65
	76

	90716
	3
	7.0
	64
	76

	90716
	4
	7.0
	64
	77

	90716
	5
	7.1
	63
	77

	90716
	6
	7.2
	65
	75

	90716
	7
	7.2
	69
	69

	90716
	8
	7.2
	75
	59

	90716
	9
	7.1
	79
	51

	90716
	10
	7.2
	82
	47

	90716
	11
	7.2
	85
	40

	90716
	12
	7.4
	87
	39

	90716
	13
	7.3
	88
	35

	90716
	14
	7.3
	88
	30

	90716
	15
	7.5
	87
	27

	90716
	16
	7.7
	86
	24

	90716
	17
	7.8
	84
	28

	90716
	18
	7.8
	82
	33

	90716
	19
	7.6
	78
	39

	90716
	20
	7.7
	75
	46

	90716
	21
	7.5
	73
	58

	90716
	22
	7.2
	70
	63

	90716
	23
	7.1
	69
	66

	90716
	24
	7.2
	68
	71

	90718
	1
	7.5
	67
	69

	90718
	2
	7.0
	66
	69

	90718
	3
	6.7
	66
	70

	90718
	4
	7.0
	65
	71

	90718
	5
	7.0
	65
	73

	90718
	6
	7.0
	66
	74

	90718
	7
	6.8
	70
	66

	90718
	8
	6.8
	73
	61

	90718
	9
	6.7
	78
	54

	90718
	10
	6.6
	83
	46

	90718
	11
	7.0
	87
	40

	90718
	12
	7.2
	91
	34

	90718
	13
	7.1
	94
	31

	90718
	14
	7.1
	91
	38

	90718
	15
	7.2
	88
	41

	90718
	16
	7.2
	87
	39

	90718
	17
	7.5
	86
	37

	90718
	18
	7.8
	82
	41

	90718
	19
	7.8
	78
	48

	90718
	20
	7.9
	75
	51

	90718
	21
	7.7
	74
	57

	90718
	22
	7.5
	72
	60

	90718
	23
	7.6
	72
	62

	90718
	24
	7.6
	70
	73

	90719
	1
	7.4
	70
	74

	90719
	2
	7.7
	69
	74

	90719
	3
	7.6
	69
	73

	90719
	4
	7.5
	69
	73

	90719
	5
	7.2
	68
	75

	90719
	6
	7.1
	68
	76

	90719
	7
	7.6
	71
	70

	90719
	8
	7.1
	76
	63

	90719
	9
	7.1
	80
	54

	90719
	10
	7.3
	84
	46

	90719
	11
	7.3
	88
	40

	90719
	12
	7.4
	92
	35

	90719
	13
	7.5
	95
	31

	90719
	14
	7.8
	96
	31

	90719
	15
	7.6
	93
	32

	90719
	16
	7.6
	90
	36

	90719
	17
	7.4
	89
	39

	90719
	18
	7.1
	85
	44

	90719
	19
	7.2
	80
	48

	90719
	20
	7.0
	77
	56

	90719
	21
	7.3
	75
	61

	90719
	22
	7.1
	74
	66

	90719
	23
	7.3
	72
	68

	90719
	24
	7.0
	72
	70

	90720
	1
	7.0
	71
	71

	90720
	2
	6.8
	71
	72

	90720
	3
	6.8
	70
	74

	90720
	4
	6.7
	69
	73

	90720
	5
	6.9
	69
	74

	90720
	6
	7.3
	71
	73

	90720
	7
	7.4
	74
	67

	90720
	8
	7.4
	79
	60

	90720
	9
	7.1
	82
	54

	90720
	10
	7.2
	85
	49

	90720
	11
	7.3
	89
	42

	90720
	12
	7.5
	93
	33

	90720
	13
	7.2
	94
	30

	90720
	14
	7.4
	93
	37

	90720
	15
	7.6
	91
	39

	90720
	16
	7.4
	91
	35

	90720
	17
	7.6
	89
	36

	90720
	18
	7.6
	86
	43

	90720
	19
	7.7
	82
	43

	90720
	20
	7.8
	78
	55

	90720
	21
	7.6
	75
	62

	90720
	22
	7.6
	73
	66

	90720
	23
	7.8
	73
	69

	90720
	24
	7.2
	72
	71

	90723
	1
	6.9
	69
	77

	90723
	2
	7.1
	68
	77

	90723
	3
	7.0
	68
	79

	90723
	4
	6.6
	67
	81

	90723
	5
	6.3
	67
	82

	90723
	6
	6.0
	68
	82

	90723
	7
	5.9
	69
	78

	90723
	8
	5.9
	71
	74

	90723
	9
	6.4
	75
	67

	90723
	10
	6.1
	79
	58

	90723
	11
	6.3
	83
	51

	90723
	12
	6.4
	86
	47

	90723
	13
	6.3
	89
	41

	90723
	14
	6.3
	89
	40

	90723
	15
	6.1
	89
	39

	90723
	16
	6.1
	88
	42

	90723
	17
	5.9
	86
	47

	90723
	18
	6.3
	82
	53

	90723
	19
	6.1
	78
	58

	90723
	20
	6.1
	74
	64

	90723
	21
	6.5
	71
	68

	90723
	22
	6.5
	69
	75

	90723
	23
	6.4
	68
	79

	90723
	24
	6.3
	68
	79

	90724
	1
	6.1
	68
	78

	90724
	2
	6.3
	68
	78

	90724
	3
	6.0
	67
	78

	90724
	4
	6.2
	67
	79

	90724
	5
	6.5
	68
	79

	90724
	6
	6.6
	68
	77

	90724
	7
	6.4
	69
	76

	90724
	8
	7.1
	72
	70

	90724
	9
	6.5
	76
	64

	90724
	10
	6.7
	78
	57

	90724
	11
	6.5
	82
	50

	90724
	12
	6.0
	84
	48

	90724
	13
	6.4
	86
	46

	90724
	14
	6.6
	86
	45

	90724
	15
	6.3
	85
	47

	90724
	16
	6.2
	83
	51

	90724
	17
	6.4
	80
	54

	90724
	18
	6.5
	78
	57

	90724
	19
	7.0
	76
	60

	90724
	20
	6.9
	73
	65

	90724
	21
	6.2
	70
	68

	90724
	22
	6.1
	68
	71

	90724
	23
	6.5
	68
	73

	90724
	24
	6.5
	67
	74

	90726
	1
	6.9
	69
	74

	90726
	2
	7.1
	69
	76

	90726
	3
	6.8
	69
	77

	90726
	4
	6.9
	68
	79

	90726
	5
	6.8
	68
	80

	90726
	6
	6.9
	68
	79

	90726
	7
	6.6
	71
	74

	90726
	8
	6.2
	74
	69

	90726
	9
	6.3
	77
	64

	90726
	10
	6.2
	81
	56

	90726
	11
	6.5
	85
	50

	90726
	12
	6.8
	88
	43

	90726
	13
	7.0
	90
	39

	90726
	14
	6.4
	88
	44

	90726
	15
	6.5
	86
	45

	90726
	16
	6.5
	84
	48

	90726
	17
	6.5
	82
	50

	90726
	18
	6.4
	81
	53

	90726
	19
	6.5
	78
	55

	90726
	20
	6.5
	74
	64

	90726
	21
	6.5
	72
	69

	90726
	22
	6.4
	70
	71

	90726
	23
	6.1
	69
	74

	90726
	24
	6.1
	69
	75

	90727
	1
	6.4
	68
	76

	90727
	2
	6.3
	68
	75

	90727
	3
	6.3
	67
	76

	90727
	4
	6.8
	66
	77

	90727
	5
	7.0
	66
	77

	90727
	6
	6.9
	67
	75

	90727
	7
	6.8
	70
	72

	90727
	8
	6.9
	74
	66

	90727
	9
	6.7
	77
	61

	90727
	10
	6.7
	80
	56

	90727
	11
	6.8
	85
	45

	90727
	12
	6.6
	87
	40

	90727
	13
	6.8
	90
	37

	90727
	14
	6.8
	89
	41

	90727
	15
	6.9
	87
	41

	90727
	16
	6.9
	86
	43

	90727
	17
	7.1
	84
	46

	90727
	18
	6.5
	81
	45

	90727
	19
	6.6
	78
	50

	90727
	20
	7.3
	74
	63

	90727
	21
	7.2
	70
	71

	90727
	22
	7.1
	69
	74

	90727
	23
	6.9
	68
	75

	90727
	24
	6.8
	67
	75

	90729
	1
	7.2
	67
	75

	90729
	2
	7.1
	67
	75

	90729
	3
	6.9
	68
	75

	90729
	4
	6.9
	67
	76

	90729
	5
	6.9
	67
	76

	90729
	6
	6.9
	67
	75

	90729
	7
	6.9
	69
	73

	90729
	8
	6.9
	70
	69

	90729
	9
	7.0
	73
	63

	90729
	10
	6.9
	75
	59

	90729
	11
	6.9
	77
	57

	90729
	12
	6.8
	80
	52

	90729
	13
	6.9
	82
	50

	90729
	14
	6.8
	82
	49

	90729
	15
	6.6
	82
	49

	90729
	16
	6.9
	81
	50

	90729
	17
	6.7
	79
	54

	90729
	18
	6.8
	78
	57

	90729
	19
	6.8
	74
	63

	90729
	20
	6.8
	70
	69

	90729
	21
	6.6
	68
	72

	90729
	22
	6.9
	68
	72

	90729
	23
	7.1
	69
	72

	90729
	24
	7.2
	69
	72

	90730
	1
	6.9
	69
	72

	90730
	2
	6.9
	69
	71

	90730
	3
	7.2
	69
	70

	90730
	4
	7.0
	69
	70

	90730
	5
	6.9
	68
	70

	90730
	6
	6.9
	68
	70

	90730
	7
	6.9
	69
	70

	90730
	8
	6.6
	70
	69

	90730
	9
	6.9
	71
	67

	90730
	10
	6.7
	74
	60

	90730
	11
	6.4
	78
	54

	90730
	12
	6.5
	80
	51

	90730
	13
	6.6
	82
	47

	90730
	14
	6.5
	84
	43

	90730
	15
	6.9
	85
	43

	90730
	16
	7.3
	84
	46

	90730
	17
	7.4
	81
	51

	90730
	18
	7.4
	78
	57

	90730
	19
	7.3
	73
	64

	90730
	20
	7.4
	70
	70

	90730
	21
	7.3
	69
	72

	90730
	22
	7.2
	67
	74

	90730
	23
	7.0
	67
	75

	90730
	24
	6.7
	67
	75

	90731
	1
	6.5
	67
	75

	90731
	2
	6.7
	68
	75

	90731
	3
	6.6
	68
	75

	90731
	4
	6.6
	68
	73

	90731
	5
	6.5
	69
	73

	90731
	6
	6.5
	69
	73

	90731
	7
	6.6
	69
	73

	90731
	8
	6.6
	71
	69

	90731
	9
	6.6
	75
	62

	90731
	10
	6.4
	78
	57

	90731
	11
	6.5
	81
	52

	90731
	12
	6.5
	83
	49

	90731
	13
	6.4
	86
	44

	90731
	14
	6.5
	86
	45

	90731
	15
	6.5
	84
	47

	90731
	16
	6.3
	82
	51

	90731
	17
	6.6
	81
	53

	90731
	18
	6.9
	77
	58

	90731
	19
	6.9
	73
	65

	90731
	20
	6.8
	70
	71

	90731
	21
	6.9
	68
	75

	90731
	22
	7.0
	67
	76

	90731
	23
	6.9
	66
	78

	90731
	24
	6.6
	66
	79

	90801
	1
	6.6
	66
	79

	90801
	2
	6.9
	67
	78

	90801
	3
	7.0
	67
	77

	90801
	4
	6.8
	67
	78

	90801
	5
	6.6
	67
	76

	90801
	6
	6.6
	68
	75

	90801
	7
	7.3
	69
	72

	90803
	8
	0.1
	70
	67

	90804
	1
	6.6
	68
	58

	90804
	7
	0.1
	65
	69

	90804
	8
	10.3
	68
	63

	90804
	9
	0.3
	72
	56

	90804
	10
	13.9
	77
	46

	90804
	11
	8.1
	85
	30

	90804
	12
	5.8
	90
	23

	90804
	13
	4.6
	94
	21

	90804
	14
	4.8
	93
	15

	90804
	15
	5.4
	92
	15

	90804
	16
	6.3
	89
	21

	90804
	17
	6.6
	87
	21

	90804
	18
	6.9
	84
	24

	90804
	19
	6.9
	80
	29

	90804
	20
	7.0
	78
	35

	90804
	21
	7.1
	76
	44

	90804
	22
	6.8
	74
	51

	90804
	23
	6.6
	72
	54

	90804
	24
	6.6
	71
	55

	90806
	1
	6.6
	68
	57

	90806
	2
	6.6
	67
	62

	90806
	3
	6.5
	65
	68

	90806
	4
	6.5
	63
	71

	90806
	5
	6.2
	63
	71

	90806
	6
	6.2
	63
	69

	90806
	7
	6.2
	67
	63

	90806
	8
	6.0
	69
	58

	90806
	9
	6.2
	73
	52

	90806
	10
	6.2
	76
	46

	90806
	11
	6.3
	78
	43

	90806
	12
	6.4
	81
	38

	90806
	13
	6.3
	82
	36

	90806
	14
	6.4
	82
	32

	90806
	15
	6.6
	82
	30

	90806
	16
	6.6
	80
	33

	90806
	17
	6.6
	79
	37

	90806
	18
	6.6
	75
	44

	90806
	19
	6.4
	71
	53

	90806
	20
	6.7
	69
	59

	90806
	21
	6.8
	67
	62

	90806
	22
	7.1
	66
	65

	90806
	23
	6.8
	66
	67

	90806
	24
	6.8
	65
	67

	90808
	1
	7.1
	62
	66

	90808
	2
	7.0
	61
	66

	90808
	3
	7.1
	60
	66

	90808
	4
	6.9
	60
	68

	90808
	5
	6.7
	59
	69

	90808
	6
	6.3
	60
	70

	90808
	7
	6.7
	65
	64

	90808
	8
	6.8
	71
	57

	90808
	9
	6.4
	73
	57

	90808
	10
	6.4
	74
	56

	90808
	11
	6.5
	77
	52

	90808
	12
	6.9
	79
	48

	90808
	13
	6.7
	80
	46

	90808
	14
	6.8
	81
	43

	90808
	15
	6.0
	82
	43

	90808
	16
	6.1
	81
	45

	90808
	17
	5.8
	80
	47

	90808
	18
	5.6
	78
	49

	90808
	19
	6.1
	73
	56

	90808
	20
	5.5
	69
	64

	90808
	21
	5.5
	68
	66

	90808
	22
	5.9
	67
	67

	90808
	23
	5.5
	66
	69

	90808
	24
	6.0
	65
	69

	90810
	1
	6.5
	64
	77

	90810
	2
	6.5
	64
	79

	90810
	3
	6.6
	63
	80

	90810
	4
	6.4
	64
	79

	90810
	5
	6.6
	64
	77

	90810
	6
	6.7
	65
	76

	90810
	7
	6.2
	66
	74

	90810
	8
	6.5
	68
	69

	90810
	9
	6.4
	71
	65

	90810
	10
	6.2
	73
	61

	90810
	11
	6.3
	76
	55

	90810
	12
	5.8
	80
	49

	90810
	13
	5.4
	83
	44

	90810
	14
	6.2
	85
	43

	90810
	15
	6.1
	82
	47

	90810
	16
	5.5
	80
	48

	90810
	17
	5.3
	77
	50

	90810
	18
	6.2
	73
	58

	90810
	19
	5.9
	69
	65

	90810
	20
	5.7
	66
	71

	90810
	21
	6.0
	65
	74

	90810
	22
	6.2
	64
	75

	90810
	23
	6.4
	64
	76

	90810
	24
	5.8
	64
	76

	90811
	1
	5.5
	63
	76

	90811
	2
	5.5
	62
	77

	90811
	3
	5.5
	62
	78

	90811
	4
	5.6
	61
	79

	90811
	5
	5.4
	61
	79

	90811
	6
	5.7
	62
	78

	90811
	7
	6.0
	64
	76

	90811
	8
	5.7
	67
	72

	90811
	9
	5.0
	71
	64

	90811
	10
	5.5
	75
	58

	90811
	11
	5.8
	77
	54

	90811
	12
	7.1
	80
	50

	90811
	13
	8.1
	81
	48

	90811
	14
	6.3
	82
	47

	90811
	15
	6.2
	81
	47

	90811
	16
	7.4
	80
	48

	90811
	17
	8.3
	77
	51

	90811
	18
	7.4
	72
	59

	90811
	19
	8.7
	68
	67

	90811
	20
	8.3
	64
	74

	90811
	21
	6.4
	63
	77

	90811
	22
	6.1
	62
	79

	90811
	23
	6.3
	61
	80

	90811
	24
	6.2
	61
	80

	90813
	1
	6.1
	62
	80

	90813
	2
	6.1
	62
	80

	90813
	3
	6.2
	62
	80

	90813
	4
	6.3
	63
	80

	90813
	5
	6.2
	63
	80

	90813
	6
	6.2
	63
	79

	90813
	7
	6.2
	63
	79

	90813
	8
	6.2
	66
	75

	90813
	9
	6.0
	71
	66

	90813
	10
	7.0
	74
	60

	90813
	11
	2.4
	78
	54

	90813
	12
	2.4
	80
	49

	90813
	13
	4.2
	82
	47

	90813
	14
	6.1
	79
	52

	90813
	15
	6.1
	78
	53

	90813
	16
	5.9
	79
	50

	90813
	17
	7.6
	78
	52

	90813
	18
	6.2
	75
	57

	90813
	19
	6.3
	71
	64

	90813
	20
	5.9
	68
	69

	90813
	21
	6.2
	65
	74

	90813
	22
	6.2
	64
	77

	90813
	23
	6.2
	64
	80

	90813
	24
	6.2
	64
	79

	90815
	1
	6.1
	65
	77

	90815
	2
	6.1
	65
	74

	90815
	3
	6.1
	66
	74

	90815
	4
	6.0
	66
	72

	90815
	5
	5.9
	66
	70

	90815
	6
	5.9
	66
	70

	90815
	7
	6.0
	67
	69

	90815
	8
	6.0
	68
	67

	90815
	9
	6.0
	70
	64

	90815
	10
	5.8
	72
	60

	90815
	11
	6.0
	76
	53

	90815
	12
	6.0
	78
	49

	90815
	13
	5.9
	81
	45

	90815
	14
	6.0
	81
	45

	90815
	15
	6.1
	80
	48

	90815
	16
	6.1
	80
	49

	90815
	17
	6.0
	78
	51

	90815
	18
	6.2
	75
	56

	90815
	19
	6.3
	70
	63

	90815
	20
	6.4
	67
	67

	90815
	21
	6.3
	66
	70

	90815
	22
	6.2
	65
	73

	90815
	23
	6.0
	64
	74

	90815
	24
	6.1
	63
	74

	90816
	1
	6.1
	63
	76

	90816
	2
	6.1
	64
	76

	90816
	3
	6.0
	64
	75

	90816
	4
	6.2
	64
	75

	90816
	5
	6.2
	64
	75

	90816
	6
	6.0
	64
	75

	90816
	7
	6.2
	65
	74

	90816
	8
	6.1
	66
	72

	90816
	9
	6.0
	68
	68

	90816
	10
	5.9
	72
	62

	90816
	11
	6.0
	75
	56

	90816
	12
	6.0
	78
	52

	90816
	13
	5.9
	81
	46

	90816
	14
	6.1
	82
	43

	90816
	15
	6.3
	80
	47

	90816
	16
	5.9
	79
	47

	90816
	17
	6.0
	77
	51

	90816
	18
	6.3
	74
	56

	90816
	19
	6.1
	70
	63

	90816
	20
	6.2
	66
	71

	90816
	21
	6.2
	64
	75

	90816
	22
	6.3
	62
	79

	90816
	23
	6.3
	61
	81

	90816
	24
	5.9
	61
	82

	90817
	1
	6.0
	62
	81

	90817
	2
	5.8
	62
	81

	90817
	3
	6.1
	62
	80

	90817
	4
	6.2
	62
	79

	90817
	5
	6.3
	62
	79

	90817
	6
	6.0
	62
	79

	90817
	7
	6.0
	62
	79

	90817
	8
	6.0
	64
	77

	90817
	9
	6.2
	66
	73

	90817
	10
	6.0
	69
	66

	90817
	11
	5.8
	73
	60

	90817
	12
	5.8
	76
	54

	90817
	13
	6.0
	79
	48

	90817
	14
	6.1
	81
	46

	90817
	15
	6.2
	81
	47

	90817
	16
	6.4
	79
	48

	90817
	17
	6.2
	77
	51

	90817
	18
	6.3
	73
	57

	90817
	19
	6.4
	68
	67

	90817
	20
	6.4
	65
	72

	90817
	21
	6.4
	64
	75

	90817
	22
	6.2
	63
	76

	90817
	23
	5.6
	62
	78

	90817
	24
	6.2
	62
	79

	90819
	1
	6.3
	62
	78

	90819
	2
	6.3
	63
	77

	90819
	3
	6.4
	63
	77

	90819
	4
	6.5
	62
	78

	90819
	5
	6.4
	62
	78

	90819
	6
	6.4
	62
	78

	90819
	7
	6.5
	63
	77

	90819
	8
	6.2
	64
	74

	90819
	9
	5.8
	66
	71

	90819
	10
	5.9
	68
	66

	90819
	11
	6.2
	72
	60

	90819
	12
	6.8
	75
	54

	90819
	13
	6.6
	78
	50

	90819
	14
	7.0
	80
	47

	90819
	15
	6.7
	81
	46

	90819
	16
	6.8
	79
	49

	90819
	17
	6.7
	76
	52

	90819
	18
	6.3
	73
	56

	90819
	19
	6.8
	68
	64

	90819
	20
	6.8
	65
	70

	90819
	21
	6.6
	64
	73

	90819
	22
	6.7
	63
	74

	90819
	23
	6.7
	62
	77

	90819
	24
	6.6
	62
	78

	90820
	1
	6.5
	61
	79

	90820
	2
	6.3
	62
	79

	90820
	3
	6.4
	62
	79

	90820
	4
	6.5
	62
	78

	90820
	5
	6.4
	62
	78

	90820
	6
	6.3
	62
	79

	90820
	7
	6.3
	62
	78

	90820
	8
	6.5
	63
	76

	90820
	9
	6.5
	65
	72

	90820
	10
	6.6
	69
	65

	90820
	11
	7.0
	72
	59

	90820
	12
	7.4
	77
	51

	90820
	13
	6.9
	79
	47

	90820
	14
	6.8
	80
	45

	90820
	15
	6.8
	79
	46

	90820
	16
	7.0
	77
	49

	90820
	17
	6.8
	75
	52

	90820
	18
	6.3
	72
	56

	90820
	19
	6.8
	68
	63

	90820
	20
	7.4
	66
	68

	90820
	21
	7.1
	65
	71

	90820
	22
	6.7
	64
	73

	90820
	23
	6.6
	63
	74

	90820
	24
	6.6
	63
	76

	90821
	1
	6.8
	62
	78

	90821
	2
	6.6
	61
	78

	90821
	3
	6.4
	61
	79

	90821
	4
	6.5
	61
	79

	90821
	5
	6.7
	61
	79

	90821
	6
	6.7
	61
	79

	90821
	7
	6.9
	65
	73

	90821
	8
	6.8
	71
	62

	90821
	9
	5.8
	73
	57

	90821
	10
	5.9
	77
	49

	90821
	11
	6.1
	80
	44

	90821
	12
	6.9
	82
	43

	90821
	13
	6.8
	80
	46

	90821
	14
	6.7
	77
	52

	90821
	15
	6.9
	73
	61

	90821
	16
	7.4
	74
	58

	90821
	17
	7.1
	78
	49

	90821
	18
	7.1
	77
	51

	90821
	19
	7.1
	76
	53

	90821
	20
	6.7
	75
	55

	90821
	21
	6.6
	70
	67

	90821
	22
	6.4
	70
	67

	90821
	23
	6.3
	71
	67

	90821
	24
	6.3
	71
	66

	90824
	1
	6.5
	66
	78

	90824
	2
	6.5
	66
	78

	90824
	3
	6.3
	65
	79

	90824
	4
	6.5
	65
	79

	90824
	5
	6.3
	64
	80

	90824
	6
	6.1
	64
	80

	90824
	7
	6.1
	69
	72

	90824
	8
	6.2
	75
	62

	90824
	9
	6.1
	77
	58

	90824
	10
	6.2
	81
	51

	90824
	11
	6.2
	83
	45

	90824
	12
	6.3
	86
	40

	90824
	13
	6.6
	87
	43

	90824
	14
	6.7
	85
	42

	90824
	15
	6.8
	86
	40

	90824
	16
	7.0
	85
	38

	90824
	17
	7.1
	84
	36

	90824
	18
	6.9
	81
	37

	90824
	19
	6.9
	77
	40

	90824
	20
	6.9
	74
	37

	90824
	21
	6.7
	72
	44

	90824
	22
	6.7
	69
	57

	90824
	23
	6.5
	68
	65

	90824
	24
	6.4
	66
	57

	90825
	1
	6.5
	64
	56

	90825
	2
	6.4
	64
	65

	90825
	3
	6.3
	64
	69

	90825
	4
	6.2
	63
	68

	90825
	5
	6.1
	62
	63

	90825
	6
	6.2
	61
	72

	90825
	7
	6.2
	67
	68

	90825
	8
	6.2
	73
	55

	90825
	9
	6.3
	82
	40

	90825
	10
	6.5
	85
	35

	90825
	11
	6.7
	89
	20

	90825
	12
	6.8
	92
	17

	90825
	13
	6.6
	93
	20

	90825
	14
	6.9
	93
	16

	90825
	15
	6.9
	92
	17

	90825
	16
	7.2
	89
	15

	90825
	17
	7.2
	88
	13

	90825
	18
	7.3
	85
	12

	90825
	19
	7.3
	79
	25

	90825
	20
	7.1
	75
	36

	90825
	21
	7.0
	72
	45

	90825
	22
	6.8
	70
	50

	90825
	23
	6.6
	67
	48

	90825
	24
	6.7
	65
	42

	90827
	1
	7.2
	68
	42

	90827
	2
	7.2
	66
	45

	90827
	3
	7.2
	65
	50

	90827
	4
	7.4
	65
	48

	90827
	5
	7.9
	64
	49

	90827
	6
	7.8
	64
	46

	90827
	7
	7.3
	69
	39

	90827
	8
	7.0
	78
	29

	90827
	9
	7.0
	85
	21

	90827
	10
	7.1
	93
	14

	90827
	11
	7.2
	99
	10

	90827
	12
	7.4
	102
	5

	90827
	13
	7.3
	103
	6

	90827
	14
	7.0
	103
	6

	90827
	15
	7.2
	101
	7

	90827
	16
	7.4
	98
	9

	90827
	17
	7.7
	95
	10

	90827
	18
	7.6
	90
	17

	90827
	19
	7.1
	83
	26

	90827
	20
	7.1
	80
	33

	90827
	21
	7.2
	78
	36

	90827
	22
	6.7
	76
	39

	90827
	23
	6.6
	73
	45

	90827
	24
	6.4
	72
	48

	90828
	1
	7.0
	70
	51

	90828
	2
	7.1
	69
	53

	90828
	3
	6.9
	68
	60

	90828
	4
	7.0
	67
	66

	90828
	5
	7.0
	67
	71

	90828
	6
	7.0
	66
	72

	90828
	7
	7.0
	70
	68

	90828
	8
	7.0
	77
	50

	90828
	9
	6.6
	86
	33

	90828
	10
	6.7
	94
	21

	90828
	11
	6.8
	98
	18

	90828
	12
	6.9
	98
	16

	90828
	13
	7.2
	99
	19

	90828
	14
	7.0
	99
	21

	90828
	15
	6.9
	99
	22

	90828
	16
	7.3
	97
	22

	90828
	17
	7.1
	98
	20

	90828
	18
	7.4
	93
	27

	90828
	19
	7.3
	86
	36

	90828
	20
	7.4
	81
	41

	90828
	21
	7.5
	79
	45

	90828
	22
	7.8
	77
	48

	90828
	23
	7.6
	76
	52

	90828
	24
	7.4
	74
	54

	90829
	1
	7.1
	72
	56

	90829
	2
	7.1
	72
	54

	90829
	3
	7.3
	70
	58

	90829
	4
	7.3
	69
	62

	90829
	5
	6.9
	69
	63

	90829
	6
	7.1
	69
	64

	90829
	7
	7.0
	75
	53

	90829
	8
	7.0
	79
	50

	90829
	9
	7.3
	87
	37

	90829
	10
	7.0
	89
	34

	90829
	11
	6.8
	94
	26

	90829
	12
	6.9
	99
	17

	90829
	13
	6.9
	102
	13

	90829
	14
	7.4
	103
	11

	90829
	15
	7.4
	103
	10

	90829
	16
	7.1
	99
	22

	90829
	17
	7.0
	95
	21

	90829
	18
	7.0
	93
	17

	90829
	19
	7.3
	89
	19

	90829
	20
	7.4
	85
	26

	90829
	21
	7.1
	81
	33

	90829
	22
	7.0
	78
	38

	90829
	23
	6.9
	75
	39

	90829
	24
	7.1
	72
	43

	90831
	1
	6.4
	71
	65

	90831
	2
	6.3
	70
	74

	90831
	3
	6.7
	69
	73

	90831
	4
	6.9
	68
	71

	90831
	5
	7.2
	68
	70

	90831
	6
	7.5
	67
	70

	90831
	7
	7.2
	72
	61

	90831
	8
	0.2
	77
	53

	90831
	9
	0.2
	85
	39

	90831
	10
	0.2
	90
	32

	90831
	11
	0.1
	93
	28

	90831
	12
	0.0
	93
	32

	90901
	9
	0.1
	78
	58

	90901
	10
	0.0
	81
	55

	90901
	11
	0.0
	84
	52

	90901
	12
	0.0
	89
	38

	90901
	13
	0.0
	92
	34

	90901
	18
	7.8
	85
	43

	90901
	19
	0.0
	79
	58

	90902
	1
	6.4
	74
	72

	90902
	7
	15.9
	72
	78

	90902
	8
	14.4
	76
	69

	90902
	9
	8.1
	81
	59

	90902
	10
	4.5
	88
	45

	90902
	11
	5.0
	92
	39

	90902
	12
	5.7
	95
	34

	90902
	13
	6.1
	98
	29

	90902
	14
	6.6
	98
	27

	90902
	15
	6.9
	97
	26

	90902
	16
	6.7
	94
	28

	90902
	17
	6.8
	91
	32

	90902
	18
	6.9
	87
	33

	90902
	19
	6.6
	81
	43

	90902
	20
	6.4
	79
	44

	90902
	21
	6.5
	77
	46

	90902
	22
	6.4
	76
	49

	90902
	23
	6.5
	76
	50

	90902
	24
	6.9
	75
	60

	90903
	1
	6.3
	74
	56

	90903
	2
	5.9
	73
	52

	90903
	3
	6.1
	72
	55

	90903
	4
	6.3
	70
	58

	90903
	5
	6.3
	70
	61

	90903
	6
	6.4
	69
	64

	90903
	7
	6.7
	74
	60

	90903
	8
	6.0
	79
	56

	90903
	9
	6.1
	83
	49

	90903
	10
	6.2
	87
	43

	90903
	11
	6.1
	92
	31

	90903
	12
	6.3
	95
	26

	90903
	13
	6.8
	97
	24

	90903
	14
	6.9
	98
	23

	90903
	15
	7.0
	96
	20

	90903
	16
	6.8
	94
	20

	90903
	17
	6.6
	92
	23

	90903
	18
	7.4
	90
	25

	90903
	19
	7.2
	85
	36

	90903
	20
	7.7
	81
	45

	90903
	21
	7.2
	78
	52

	90903
	22
	7.3
	77
	55

	90903
	23
	7.2
	76
	55

	90903
	24
	7.5
	74
	57

	90904
	1
	7.3
	74
	62

	90904
	2
	7.8
	73
	70

	90904
	3
	7.4
	72
	75

	90904
	4
	6.4
	71
	76

	90904
	5
	6.7
	70
	77

	90904
	6
	6.7
	70
	78

	90904
	7
	7.1
	73
	74

	90904
	8
	7.3
	80
	58

	90904
	9
	7.2
	83
	49

	90904
	10
	6.4
	86
	42

	90904
	11
	6.7
	90
	38

	90904
	12
	6.6
	93
	33

	90904
	13
	6.8
	96
	28

	90904
	14
	6.9
	96
	29

	90904
	15
	6.9
	95
	33

	90904
	16
	6.7
	91
	35

	90904
	17
	7.2
	89
	32

	90904
	18
	7.1
	85
	41

	90904
	19
	6.8
	81
	46

	90904
	20
	7.2
	80
	48

	90904
	21
	7.3
	78
	53

	90904
	22
	7.4
	76
	62

	90904
	23
	7.3
	73
	64

	90904
	24
	7.2
	73
	69

	90906
	1
	7.2
	62
	60

	90906
	2
	7.1
	62
	61

	90906
	3
	7.3
	61
	65

	90906
	4
	7.2
	61
	67

	90906
	5
	7.0
	61
	69

	90906
	6
	7.0
	60
	71

	90906
	7
	6.9
	66
	64

	90906
	8
	6.8
	70
	69

	90906
	9
	6.6
	71
	69

	90906
	10
	6.5
	75
	60

	90906
	11
	6.6
	79
	54

	90906
	12
	6.7
	83
	46

	90906
	13
	6.7
	86
	35

	90906
	14
	6.9
	88
	34

	90906
	15
	6.7
	87
	40

	90906
	16
	6.9
	85
	42

	90906
	17
	7.1
	82
	46

	90906
	18
	7.3
	78
	45

	90906
	19
	7.3
	73
	54

	90906
	20
	7.3
	71
	58

	90906
	21
	7.3
	70
	62

	90906
	22
	7.3
	68
	65

	90906
	23
	7.0
	66
	67

	90906
	24
	6.4
	65
	68

	90907
	1
	6.7
	64
	70

	90907
	2
	6.4
	63
	72

	90907
	3
	7.3
	62
	74

	90907
	4
	6.8
	62
	77

	90907
	5
	6.7
	62
	79

	90907
	6
	6.7
	63
	80

	90907
	7
	7.0
	65
	72

	90907
	8
	7.2
	69
	70

	90907
	9
	7.0
	74
	63

	90907
	10
	7.1
	77
	57

	90907
	11
	7.0
	80
	51

	90907
	12
	6.9
	83
	40

	90907
	13
	7.0
	85
	39

	90907
	14
	7.2
	84
	40

	90907
	15
	7.1
	84
	41

	90907
	16
	7.1
	82
	45

	90907
	17
	6.9
	80
	48

	90907
	18
	7.4
	78
	52

	90907
	19
	7.5
	75
	58

	90907
	20
	7.6
	72
	62

	90907
	21
	7.6
	70
	67

	90907
	22
	7.5
	69
	73

	90907
	23
	6.9
	68
	78

	90907
	24
	7.0
	66
	79

	90908
	1
	6.4
	66
	79

	90908
	2
	6.4
	66
	79

	90908
	3
	6.9
	65
	77

	90908
	4
	6.8
	66
	76

	90908
	5
	6.7
	66
	75

	90908
	6
	6.5
	66
	75

	90908
	7
	6.5
	67
	73

	90908
	8
	6.7
	70
	67

	90908
	9
	6.0
	72
	63

	90908
	10
	6.3
	74
	58

	90908
	11
	6.3
	78
	50

	90908
	12
	6.5
	81
	41

	90908
	13
	6.5
	83
	40

	90908
	14
	6.4
	84
	40

	90908
	15
	6.5
	83
	41

	90908
	16
	6.4
	81
	48

	90908
	17
	6.5
	79
	50

	90908
	18
	6.7
	75
	55

	90908
	19
	6.8
	72
	64

	90908
	20
	6.8
	70
	68

	90908
	21
	6.6
	69
	70

	90908
	22
	6.4
	68
	72

	90908
	23
	6.3
	67
	74

	90908
	24
	6.1
	66
	75

	90909
	1
	6.4
	66
	76

	90909
	2
	6.3
	65
	78

	90909
	3
	6.3
	64
	79

	90909
	4
	6.3
	64
	79

	90909
	5
	6.3
	65
	78

	90909
	6
	6.2
	65
	78

	90909
	7
	6.2
	66
	76

	90909
	8
	6.3
	67
	73

	90909
	9
	6.5
	72
	65

	90909
	10
	6.3
	75
	59

	90909
	11
	6.3
	79
	53

	90909
	12
	6.3
	82
	45

	90909
	13
	6.4
	86
	34

	90909
	14
	6.5
	88
	34

	90909
	15
	6.5
	87
	37

	90909
	16
	6.2
	85
	41

	90909
	17
	6.4
	82
	47

	90909
	18
	6.5
	78
	52

	90909
	19
	6.4
	74
	59

	90909
	20
	6.4
	71
	66

	90909
	21
	6.3
	69
	74

	90909
	22
	6.3
	68
	76

	90909
	23
	6.3
	67
	78

	90909
	24
	6.1
	67
	79

	90910
	1
	6.3
	65
	80

	90910
	2
	6.2
	64
	81

	90910
	3
	6.2
	63
	81

	90910
	4
	6.2
	63
	82

	90910
	5
	6.2
	63
	84

	90910
	6
	6.2
	63
	84

	90910
	7
	6.4
	66
	79

	90910
	8
	6.3
	72
	68

	90910
	9
	6.3
	76
	55

	90910
	10
	6.3
	79
	50

	90910
	11
	6.4
	84
	40

	90910
	12
	6.5
	89
	32

	90910
	13
	6.7
	92
	27

	90910
	14
	6.7
	93
	27

	90910
	15
	6.6
	91
	31

	90910
	16
	6.4
	88
	32

	90910
	17
	6.4
	84
	38

	90910
	18
	6.3
	80
	45

	90910
	19
	6.5
	76
	52

	90910
	20
	6.7
	74
	55

	90910
	21
	5.7
	73
	58

	90910
	22
	6.0
	72
	61

	90910
	23
	6.5
	71
	62

	90910
	24
	6.5
	70
	65

	90911
	1
	6.3
	69
	66

	90911
	2
	6.4
	68
	66

	90911
	3
	6.5
	68
	65

	90911
	4
	6.7
	67
	65

	90911
	5
	6.8
	67
	64

	90911
	6
	6.5
	68
	64

	90911
	7
	6.6
	69
	63

	90911
	8
	6.4
	77
	53

	90911
	9
	6.4
	80
	46

	90911
	10
	6.3
	82
	44

	90911
	11
	6.4
	85
	42

	90911
	12
	6.5
	86
	40

	90911
	13
	6.6
	87
	46

	90911
	14
	6.3
	87
	42

	90911
	15
	6.5
	86
	39

	90911
	16
	6.4
	85
	38

	90911
	17
	6.7
	82
	39

	90911
	18
	6.5
	79
	44

	90911
	19
	6.7
	74
	58

	90911
	20
	6.6
	72
	62

	90911
	21
	6.6
	71
	63

	90911
	22
	6.5
	70
	66

	90911
	23
	6.6
	69
	70

	90911
	24
	6.2
	68
	75

	90912
	1
	6.1
	67
	77

	90912
	2
	6.3
	66
	79

	90912
	3
	6.2
	66
	80

	90912
	4
	6.1
	65
	81

	90912
	5
	6.2
	64
	81

	90912
	6
	6.3
	64
	82

	90912
	7
	6.2
	65
	81

	90912
	8
	6.1
	68
	76

	90912
	9
	6.2
	70
	72

	90912
	10
	6.1
	74
	65

	90912
	11
	6.2
	77
	59

	90912
	12
	6.4
	81
	51

	90912
	13
	6.6
	82
	49

	90912
	14
	6.4
	82
	51

	90912
	15
	6.5
	81
	50

	90912
	16
	6.4
	81
	50

	90912
	17
	6.5
	78
	53

	90912
	18
	6.5
	73
	60

	90912
	19
	6.7
	69
	69

	90912
	20
	6.5
	67
	73

	90912
	21
	6.3
	66
	75

	90912
	22
	6.2
	66
	76

	90912
	23
	6.2
	66
	76

	90912
	24
	6.3
	65
	76

	90913
	1
	6.3
	66
	76

	90913
	2
	6.3
	66
	75

	90913
	3
	6.6
	65
	74

	90913
	4
	6.7
	65
	74

	90913
	5
	6.3
	65
	74

	90913
	6
	6.4
	66
	74

	90913
	7
	6.4
	66
	73

	90913
	8
	6.3
	68
	70

	90913
	9
	6.3
	69
	66

	90913
	10
	6.1
	70
	64

	90913
	11
	6.1
	72
	59

	90913
	12
	6.1
	74
	54

	90913
	13
	6.1
	76
	52

	90913
	14
	6.2
	77
	50

	90913
	15
	6.4
	76
	51

	90913
	16
	6.5
	75
	53

	90913
	17
	6.5
	73
	55

	90913
	18
	6.3
	71
	61

	90913
	19
	6.5
	68
	67

	90913
	20
	6.5
	68
	68

	90913
	21
	6.4
	67
	68

	90913
	22
	6.4
	67
	69

	90913
	23
	6.5
	67
	68

	90913
	24
	6.4
	67
	67

	90915
	1
	6.3
	61
	79

	90915
	2
	6.4
	60
	79

	90915
	3
	6.3
	59
	81

	90915
	4
	6.3
	59
	82

	90915
	5
	6.4
	59
	82

	90915
	6
	6.4
	59
	83

	90915
	7
	6.2
	62
	79

	90915
	8
	6.2
	67
	71

	90915
	9
	6.0
	69
	66

	90915
	10
	6.5
	73
	57

	90915
	11
	6.5
	76
	49

	90915
	12
	6.5
	78
	45

	90915
	18
	6.1
	74
	53

	90915
	19
	5.9
	70
	63

	90915
	20
	6.6
	68
	72

	90915
	21
	6.6
	67
	74

	90915
	22
	6.6
	67
	75

	90915
	23
	6.2
	65
	76

	90915
	24
	6.3
	64
	77

	90917
	1
	7.4
	66
	74

	90917
	2
	7.0
	65
	74

	90917
	3
	6.9
	64
	76

	90917
	4
	6.7
	63
	78

	90917
	5
	6.7
	62
	80

	90917
	6
	6.9
	62
	82

	90917
	7
	6.1
	67
	75

	90917
	8
	6.6
	74
	62

	90917
	9
	7.7
	77
	56

	90917
	10
	7.4
	81
	51

	90917
	11
	7.2
	85
	44

	90917
	12
	6.7
	88
	41

	90917
	13
	7.0
	90
	39

	90917
	14
	7.0
	89
	39

	90917
	15
	6.4
	87
	40

	90917
	16
	6.2
	85
	42

	90917
	17
	6.5
	82
	48

	90917
	18
	6.7
	78
	53

	90917
	19
	6.2
	75
	59

	90917
	20
	6.6
	72
	61

	90917
	21
	6.7
	71
	64

	90917
	22
	6.5
	70
	68

	90917
	23
	7.5
	69
	70

	90917
	24
	7.6
	69
	70

	90918
	1
	7.1
	68
	73

	90918
	2
	7.5
	66
	76

	90918
	3
	7.7
	65
	77

	90918
	4
	7.7
	64
	79

	90918
	5
	7.6
	63
	79

	90918
	6
	7.4
	63
	81

	90918
	7
	7.6
	67
	78

	90918
	8
	7.4
	70
	74

	90918
	9
	7.1
	74
	69

	90918
	10
	6.7
	77
	64

	90918
	11
	7.0
	82
	54

	90918
	12
	6.8
	88
	43

	90918
	13
	7.2
	91
	38

	90918
	14
	6.8
	92
	38

	90918
	15
	6.1
	92
	35

	90918
	16
	6.3
	90
	36

	90918
	17
	6.4
	87
	41

	90918
	18
	6.5
	81
	52

	90918
	19
	6.8
	76
	62

	90918
	20
	6.5
	73
	70

	90918
	21
	6.4
	70
	75

	90918
	22
	6.5
	67
	79

	90918
	23
	6.3
	66
	82

	90918
	24
	6.4
	67
	81

	90919
	1
	6.2
	68
	80

	90919
	2
	6.4
	69
	78

	90919
	3
	6.4
	68
	79

	90919
	4
	6.3
	68
	79

	90919
	5
	6.3
	68
	79

	90919
	6
	6.3
	67
	80

	90919
	7
	6.4
	67
	79

	90919
	8
	6.5
	70
	75

	90919
	9
	6.4
	75
	66

	90919
	10
	6.9
	78
	60

	90919
	11
	6.9
	82
	52

	90919
	12
	7.0
	86
	41

	90919
	13
	7.0
	88
	37

	90919
	14
	7.1
	88
	40

	90919
	15
	6.8
	85
	47

	90919
	16
	6.9
	84
	47

	90919
	17
	7.0
	82
	50

	90919
	18
	6.8
	75
	60

	90919
	19
	6.7
	71
	70

	90919
	20
	6.7
	69
	73

	90919
	21
	6.7
	68
	76

	90919
	22
	6.6
	67
	77

	90919
	23
	6.6
	67
	78

	90919
	24
	6.5
	66
	79

	90920
	1
	6.4
	66
	80

	90920
	2
	6.3
	65
	81

	90920
	3
	6.3
	65
	81

	90920
	4
	6.4
	65
	82

	90920
	5
	6.3
	65
	82

	90920
	6
	6.4
	65
	81

	90920
	7
	6.6
	65
	82

	90920
	8
	6.3
	67
	79

	90920
	9
	6.3
	72
	69

	90920
	10
	6.2
	76
	61

	90920
	11
	6.4
	79
	54

	90920
	12
	6.5
	83
	44

	90920
	13
	6.7
	86
	38

	90920
	14
	6.7
	88
	35

	90920
	15
	6.7
	87
	39

	90920
	16
	6.7
	84
	44

	90920
	17
	6.5
	81
	50

	90920
	18
	6.6
	75
	59

	90920
	19
	6.9
	71
	68

	90920
	20
	6.6
	68
	74

	90920
	21
	6.6
	67
	77

	90920
	22
	6.6
	66
	78

	90920
	23
	6.6
	65
	80

	90920
	24
	6.5
	64
	80

	90921
	1
	6.5
	63
	81

	90921
	2
	6.4
	61
	82

	90921
	3
	6.5
	61
	83

	90921
	4
	6.6
	62
	83

	90921
	5
	6.4
	62
	84

	90921
	6
	6.3
	62
	84

	90921
	7
	6.3
	62
	85

	90921
	8
	6.2
	64
	84

	90921
	9
	6.2
	66
	79

	90921
	10
	6.2
	71
	68

	90921
	11
	6.4
	76
	59

	90921
	12
	6.5
	80
	49

	90921
	13
	6.8
	84
	37

	90921
	14
	6.8
	87
	37

	90921
	15
	6.9
	85
	42

	90921
	16
	7.0
	81
	47

	90921
	17
	7.0
	77
	54

	90921
	18
	6.9
	72
	62

	90921
	19
	6.7
	69
	67

	90921
	20
	6.6
	68
	72

	90921
	21
	6.6
	67
	75

	90921
	22
	6.7
	66
	77

	90921
	23
	6.8
	65
	77

	90921
	24
	6.8
	64
	78

	90922
	1
	6.5
	63
	79

	90922
	2
	6.5
	62
	81

	90922
	3
	6.6
	62
	82

	90922
	4
	6.5
	61
	83

	90922
	5
	6.6
	59
	83

	90922
	6
	6.4
	59
	84

	90922
	7
	6.7
	63
	80

	90922
	8
	6.6
	70
	70

	90922
	9
	6.5
	75
	62

	90922
	10
	6.2
	81
	52

	90922
	11
	6.2
	84
	44

	90922
	12
	6.5
	89
	36

	90922
	13
	6.9
	93
	32

	90922
	14
	6.8
	94
	31

	90922
	15
	7.0
	93
	30

	90922
	16
	7.0
	89
	36

	90922
	17
	7.1
	85
	43

	90922
	18
	7.3
	79
	51

	90922
	19
	7.2
	75
	59

	90922
	20
	6.9
	73
	63

	90922
	21
	7.1
	71
	68

	90922
	22
	7.2
	68
	69

	90922
	23
	6.9
	67
	73

	90922
	24
	15.7
	67
	71

	90924
	1
	6.7
	67
	45

	90924
	2
	7.4
	67
	42

	90924
	3
	8.2
	66
	41

	90924
	4
	8.6
	65
	40

	90924
	5
	8.4
	65
	39

	90924
	6
	8.3
	66
	37

	90924
	7
	8.4
	69
	34

	90924
	8
	8.1
	78
	26

	90924
	9
	8.0
	86
	16

	90924
	10
	7.6
	92
	12

	90924
	11
	7.6
	94
	10

	90924
	12
	7.7
	97
	9

	90924
	13
	7.8
	99
	9

	90924
	14
	7.9
	100
	5

	90924
	15
	8.0
	99
	11

	90924
	16
	8.0
	97
	12

	90924
	17
	8.0
	93
	12

	90924
	18
	8.1
	89
	19

	90924
	19
	8.0
	82
	33

	90924
	20
	8.1
	79
	33

	90924
	21
	11.1
	77
	35

	90924
	22
	7.2
	75
	39

	90924
	23
	5.8
	71
	41

	90924
	24
	6.7
	70
	44

	90925
	1
	5.9
	69
	44

	90925
	2
	6.4
	65
	52

	90925
	3
	6.6
	64
	55

	90925
	4
	6.7
	63
	56

	90925
	5
	6.7
	62
	68

	90925
	6
	6.6
	62
	68

	90925
	7
	6.6
	66
	58

	90925
	8
	6.9
	72
	46

	90925
	9
	7.0
	80
	36

	90925
	10
	7.4
	84
	31

	90925
	11
	7.4
	90
	25

	90925
	12
	7.0
	94
	18

	90925
	13
	7.1
	97
	13

	90925
	14
	7.1
	97
	21

	90925
	15
	7.1
	96
	20

	90925
	16
	7.2
	93
	21

	90925
	17
	7.2
	91
	22

	90925
	18
	7.3
	86
	27

	90925
	19
	7.2
	81
	35

	90925
	20
	7.1
	78
	39

	90925
	21
	7.1
	75
	45

	90925
	22
	6.8
	73
	49

	90925
	23
	6.9
	70
	48

	90925
	24
	6.7
	69
	48

	90926
	1
	6.6
	67
	54

	90926
	2
	6.6
	66
	55

	90926
	3
	6.5
	64
	59

	90926
	4
	6.4
	64
	66

	90926
	5
	5.7
	64
	68

	90926
	6
	6.1
	62
	67

	90926
	7
	6.3
	66
	65

	90926
	8
	6.2
	71
	65

	90926
	9
	6.1
	75
	59

	90926
	10
	6.4
	80
	54

	90926
	11
	6.6
	85
	45

	90926
	12
	6.9
	89
	38

	90926
	13
	6.8
	91
	38

	90926
	14
	6.9
	88
	42

	90926
	15
	6.9
	87
	38

	90926
	16
	6.8
	89
	32

	90926
	17
	6.9
	89
	31

	90926
	18
	6.9
	84
	35

	90926
	19
	7.0
	79
	47

	90926
	20
	6.7
	74
	60

	90926
	21
	6.7
	71
	67

	90926
	22
	6.5
	69
	71

	90926
	23
	6.4
	69
	73

	90926
	24
	6.3
	68
	76

	90928
	1
	6.4
	64
	81

	90928
	2
	6.3
	64
	82

	90928
	3
	6.5
	64
	81

	90928
	4
	6.4
	64
	81

	90928
	5
	6.2
	64
	80

	90928
	6
	6.3
	64
	80

	90928
	7
	6.3
	64
	79

	90928
	8
	6.2
	66
	77

	90928
	9
	6.1
	68
	73

	90928
	10
	6.3
	72
	65

	90928
	11
	6.2
	75
	58

	90928
	12
	6.0
	76
	55

	90928
	13
	6.3
	77
	50

	90928
	14
	6.1
	81
	41

	90928
	15
	6.5
	81
	49

	90928
	16
	6.4
	78
	52

	90928
	17
	6.5
	76
	56

	90928
	18
	6.6
	70
	65

	90928
	19
	6.6
	66
	73

	90928
	20
	6.5
	64
	76

	90928
	21
	6.5
	63
	77

	90928
	22
	6.4
	63
	78

	90928
	23
	6.7
	62
	79

	90928
	24
	6.2
	61
	80

	90930
	1
	11.9
	64
	69

	90930
	2
	10.1
	64
	67

	90930
	3
	6.2
	64
	66

	90930
	4
	5.9
	65
	64

	90930
	5
	6.0
	63
	69

	90930
	6
	6.2
	61
	75

	90930
	7
	6.3
	62
	74

	90930
	8
	6.1
	67
	63

	90930
	9
	6.5
	70
	55

	90930
	10
	0.0
	72
	49

	90930
	20
	13.4
	67
	30

	90930
	21
	10.1
	65
	32

	90930
	22
	10.6
	63
	37

	90930
	23
	6.6
	61
	43

	90930
	24
	0.1
	60
	46

	91002
	1
	6.9
	61
	39

	91002
	2
	6.8
	59
	44

	91002
	3
	6.9
	59
	45

	91002
	4
	7.3
	57
	50

	91002
	5
	7.4
	56
	51

	91002
	6
	7.4
	55
	49

	91002
	7
	7.5
	58
	43

	91002
	8
	7.6
	67
	32

	91002
	9
	7.8
	75
	20

	91002
	10
	7.6
	78
	21

	91002
	11
	7.7
	83
	13

	91002
	12
	8.0
	86
	8

	91002
	13
	8.2
	86
	9

	91002
	14
	8.1
	88
	10

	91002
	15
	8.1
	86
	10

	91002
	16
	7.7
	84
	24

	91002
	17
	7.9
	82
	23

	91002
	18
	8.2
	75
	30

	91002
	19
	8.1
	72
	35

	91002
	20
	8.2
	70
	38

	91002
	21
	8.1
	67
	39

	91002
	22
	7.7
	67
	46

	91002
	23
	7.6
	66
	60

	91002
	24
	7.4
	63
	65

	91005
	1
	7.2
	55
	66

	91005
	2
	7.1
	55
	65

	91005
	3
	7.1
	54
	64

	91005
	4
	7.1
	54
	63

	91005
	5
	7.0
	54
	63

	91005
	6
	7.1
	54
	63

	91005
	7
	7.1
	55
	61

	91005
	8
	6.9
	58
	56

	91005
	9
	6.9
	62
	48

	91005
	10
	7.0
	65
	43

	91005
	11
	7.0
	67
	40

	91005
	12
	7.2
	70
	35

	91005
	13
	7.2
	71
	33

	91005
	14
	7.4
	72
	32

	91005
	15
	7.5
	69
	43

	91005
	16
	7.6
	68
	46

	91005
	17
	7.6
	67
	47

	91005
	18
	7.8
	64
	56

	91005
	19
	7.5
	61
	63

	91005
	20
	7.5
	60
	64

	91005
	21
	7.3
	59
	64

	91005
	22
	7.4
	57
	67

	91005
	23
	7.3
	56
	69

	91005
	24
	7.3
	55
	69

	91006
	1
	7.3
	53
	73

	91006
	2
	7.2
	53
	73

	91006
	3
	7.3
	52
	75

	91006
	4
	7.3
	52
	77

	91006
	5
	7.3
	51
	78

	91006
	6
	7.2
	51
	78

	91006
	7
	7.3
	52
	74

	91006
	8
	7.2
	59
	66

	91006
	9
	7.2
	64
	56

	91006
	10
	7.3
	68
	51

	91006
	11
	7.2
	68
	49

	91006
	12
	6.6
	71
	43

	91006
	13
	7.3
	73
	39

	91006
	14
	7.4
	73
	41

	91006
	15
	7.5
	71
	50

	91006
	16
	7.3
	69
	52

	91006
	17
	7.3
	67
	53

	91006
	18
	7.7
	65
	55

	91006
	19
	7.8
	63
	60

	91006
	20
	7.7
	61
	65

	91006
	21
	7.6
	60
	68

	91006
	22
	7.5
	58
	71

	91006
	23
	7.5
	56
	73

	91006
	24
	7.5
	56
	75

	91007
	1
	7.5
	55
	76

	91007
	2
	7.3
	55
	76

	91007
	3
	7.1
	56
	76

	91007
	4
	7.3
	55
	78

	91007
	5
	7.6
	55
	77

	91007
	6
	7.5
	55
	76

	91007
	7
	7.3
	56
	73

	91007
	8
	7.2
	62
	64

	91007
	9
	7.0
	66
	55

	91007
	10
	6.8
	65
	53

	91007
	11
	6.8
	69
	48

	91007
	12
	6.7
	70
	46

	91007
	13
	6.6
	70
	47

	91007
	14
	6.7
	71
	47

	91007
	15
	7.0
	70
	48

	91007
	16
	7.0
	69
	50

	91007
	17
	7.8
	67
	54

	91007
	18
	7.7
	64
	64

	91007
	19
	8.0
	62
	68

	91007
	20
	8.0
	61
	70

	91007
	21
	7.8
	59
	72

	91007
	22
	8.1
	57
	73

	91007
	23
	8.3
	56
	76

	91007
	24
	8.5
	55
	77

	91009
	1
	6.9
	56
	78

	91009
	2
	6.7
	55
	80

	91009
	3
	6.7
	54
	81

	91009
	4
	6.9
	54
	82

	91009
	5
	6.9
	55
	81

	91009
	6
	6.8
	57
	79

	91009
	7
	7.5
	58
	77

	91009
	8
	7.7
	59
	73

	91009
	9
	7.6
	62
	70

	91009
	10
	7.4
	64
	65

	91009
	11
	7.3
	69
	56

	91009
	12
	7.6
	71
	51

	91009
	13
	7.4
	73
	47

	91009
	14
	6.7
	75
	41

	91009
	15
	6.8
	74
	47

	91009
	16
	6.3
	73
	48

	91009
	17
	7.0
	71
	52

	91009
	18
	6.8
	65
	65

	91009
	19
	6.3
	62
	72

	91009
	20
	6.1
	61
	76

	91009
	21
	6.8
	60
	77

	91009
	22
	6.8
	59
	78

	91009
	23
	6.8
	59
	79

	91009
	24
	6.7
	57
	80

	91010
	1
	6.6
	56
	81

	91010
	2
	6.7
	56
	81

	91010
	3
	6.5
	58
	81

	91010
	4
	6.6
	58
	80

	91010
	5
	6.8
	58
	80

	91010
	6
	6.8
	57
	79

	91010
	7
	6.8
	57
	79

	91010
	8
	6.6
	59
	77

	91010
	9
	7.0
	62
	74

	91010
	10
	6.7
	64
	69

	91010
	11
	6.3
	68
	62

	91010
	12
	6.7
	72
	54

	91010
	13
	7.0
	72
	50

	91010
	14
	6.9
	75
	48

	91010
	15
	6.8
	74
	50

	91010
	16
	6.9
	69
	54

	91010
	17
	7.1
	65
	60

	91010
	18
	7.2
	62
	67

	91010
	19
	7.0
	60
	71

	91010
	20
	7.0
	59
	72

	91010
	21
	6.9
	59
	72

	91010
	22
	6.9
	58
	73

	91010
	23
	6.8
	59
	72

	91010
	24
	6.8
	59
	71

	91013
	1
	6.9
	60
	69

	91013
	2
	7.1
	60
	73

	91013
	3
	7.2
	59
	75

	91013
	4
	6.9
	59
	77

	91013
	5
	7.0
	59
	75

	91013
	6
	7.0
	59
	77

	91013
	7
	6.9
	58
	84

	91013
	8
	6.9
	59
	81

	91013
	9
	6.6
	61
	77

	91013
	10
	6.1
	64
	70

	91013
	11
	5.8
	65
	70

	91013
	12
	6.6
	66
	68

	91013
	13
	7.5
	65
	71

	91013
	14
	7.1
	67
	62

	91013
	15
	6.8
	65
	69

	91013
	16
	7.1
	66
	66

	91013
	17
	7.1
	65
	70

	91013
	18
	7.2
	65
	69

	91013
	19
	7.1
	63
	75

	91013
	20
	6.6
	62
	82

	91013
	21
	6.5
	61
	84

	91013
	22
	6.7
	61
	85

	91013
	23
	6.5
	60
	85

	91013
	24
	6.5
	60
	86

	91014
	1
	6.6
	60
	87

	91014
	2
	6.7
	59
	86

	91014
	3
	6.5
	59
	87

	91014
	4
	6.4
	59
	87

	91014
	5
	6.4
	60
	86

	91014
	6
	6.5
	60
	86

	91014
	7
	6.5
	60
	86

	91014
	8
	6.5
	60
	85

	91014
	9
	6.8
	61
	83

	91014
	10
	7.0
	63
	81

	91014
	11
	6.7
	66
	79

	91014
	12
	6.9
	67
	78

	91014
	13
	6.3
	67
	77

	91014
	14
	6.9
	66
	81

	91014
	15
	6.7
	67
	80

	91014
	16
	6.8
	67
	81

	91014
	17
	6.9
	67
	80

	91014
	18
	7.0
	66
	81

	91014
	19
	6.9
	64
	84

	91014
	20
	6.8
	64
	85

	91014
	21
	6.7
	63
	86

	91014
	22
	6.7
	62
	86

	91014
	23
	6.7
	62
	87

	91014
	24
	6.7
	63
	87

	91016
	1
	7.5
	64
	82

	91016
	2
	7.2
	63
	82

	91016
	3
	7.3
	62
	83

	91016
	4
	7.4
	62
	82

	91016
	5
	7.2
	61
	79

	91016
	6
	7.3
	61
	76

	91016
	7
	7.3
	62
	72

	91016
	8
	7.8
	68
	64

	91016
	9
	8.2
	77
	47

	91016
	10
	8.3
	83
	36

	91016
	11
	8.0
	91
	24

	91016
	12
	7.3
	94
	20

	91016
	13
	8.1
	96
	16

	91016
	14
	8.5
	97
	15

	91016
	15
	8.7
	97
	15

	91016
	16
	8.4
	95
	20

	91016
	17
	8.4
	90
	26

	91016
	18
	8.6
	84
	32

	91016
	19
	8.7
	80
	37

	91016
	20
	8.8
	77
	43

	91016
	21
	8.6
	74
	47

	91016
	22
	8.7
	70
	55

	91016
	23
	8.4
	70
	55

	91016
	24
	8.1
	68
	61

	91018
	1
	6.6
	62
	87

	91018
	2
	6.6
	60
	88

	91018
	3
	6.7
	61
	88

	91018
	4
	6.9
	61
	89

	91018
	5
	6.2
	61
	89

	91018
	6
	6.8
	60
	89

	91018
	7
	7.2
	60
	89

	91018
	8
	6.7
	60
	89

	91018
	9
	6.2
	61
	89

	91018
	10
	6.3
	65
	80

	91018
	11
	6.4
	71
	65

	91018
	12
	6.6
	74
	57

	91018
	13
	6.8
	75
	55

	91018
	14
	6.8
	75
	55

	91018
	15
	6.8
	75
	55

	91018
	16
	6.8
	74
	56

	91018
	17
	7.0
	72
	61

	91018
	18
	7.1
	67
	73

	91018
	19
	6.9
	64
	78

	91018
	20
	6.7
	63
	79

	91018
	21
	6.7
	63
	79

	91018
	22
	6.7
	63
	80

	91018
	23
	6.8
	63
	79

	91018
	24
	6.8
	63
	79

	91019
	1
	6.7
	63
	77

	91019
	2
	6.7
	63
	75

	91019
	3
	6.7
	63
	73

	91019
	4
	6.8
	64
	71

	91019
	5
	6.6
	64
	72

	91019
	6
	6.7
	64
	70

	91019
	7
	6.8
	64
	71

	91019
	8
	6.7
	65
	70

	91019
	9
	6.7
	66
	66

	91019
	10
	6.6
	67
	63

	91019
	11
	6.6
	71
	58

	91019
	12
	6.7
	72
	54

	91019
	13
	7.0
	71
	56

	91019
	14
	7.0
	71
	60

	91019
	15
	7.1
	70
	60

	91019
	16
	7.3
	69
	62

	91019
	17
	7.0
	67
	65

	91019
	18
	7.1
	64
	65

	91019
	19
	7.2
	64
	59

	91019
	20
	7.2
	63
	67

	91019
	21
	6.9
	62
	69

	91019
	22
	6.9
	61
	71

	91019
	23
	7.0
	60
	75

	91019
	24
	6.9
	59
	75

	91021
	1
	7.1
	56
	75

	91021
	2
	7.1
	55
	76

	91021
	3
	7.1
	54
	77

	91021
	4
	7.1
	53
	79

	91021
	5
	7.0
	53
	80

	91021
	6
	7.0
	53
	80

	91021
	7
	7.0
	54
	77

	91021
	8
	7.2
	59
	69

	91021
	9
	7.1
	67
	52

	91021
	10
	6.9
	74
	39

	91021
	11
	7.0
	77
	33

	91021
	12
	7.1
	80
	28

	91021
	13
	7.4
	81
	26

	91021
	14
	7.4
	81
	25

	91021
	15
	7.5
	82
	25

	91021
	16
	7.4
	80
	29

	91021
	17
	7.7
	77
	32

	91021
	18
	7.6
	73
	39

	91021
	19
	7.7
	69
	46

	91021
	20
	7.5
	66
	52

	91021
	21
	7.6
	63
	59

	91021
	22
	7.4
	61
	63

	91021
	23
	7.3
	59
	65

	91021
	24
	7.2
	58
	66

	91023
	1
	7.0
	58
	77

	91023
	2
	6.8
	58
	81

	91023
	3
	6.9
	57
	82

	91023
	4
	6.8
	56
	81

	91023
	5
	6.7
	56
	79

	91023
	6
	7.0
	56
	78

	91023
	7
	7.3
	56
	78

	91023
	8
	8.1
	62
	68

	91023
	9
	7.5
	67
	56

	91023
	10
	7.2
	74
	42

	91023
	11
	7.7
	83
	28

	91023
	12
	8.5
	87
	17

	91023
	13
	8.1
	89
	14

	91023
	14
	8.5
	88
	20

	91023
	15
	7.9
	84
	29

	91023
	16
	8.4
	83
	25

	91023
	17
	8.7
	80
	29

	91023
	18
	8.4
	74
	53

	91023
	19
	8.6
	70
	53

	91023
	20
	8.6
	68
	54

	91023
	21
	8.4
	66
	58

	91023
	22
	7.8
	64
	64

	91023
	23
	7.9
	62
	63

	91023
	24
	7.8
	61
	65

	91026
	1
	7.2
	60
	74

	91026
	2
	7.2
	59
	68

	91026
	3
	7.3
	59
	62

	91026
	4
	7.5
	58
	54

	91026
	5
	8.1
	59
	46

	91026
	6
	8.2
	58
	46

	91026
	7
	8.3
	58
	46

	91026
	8
	9.0
	63
	44

	91026
	9
	8.4
	70
	33

	91026
	10
	8.3
	79
	18

	91026
	11
	8.3
	85
	7

	91026
	12
	8.6
	89
	4

	91026
	13
	8.9
	91
	3

	91026
	14
	9.1
	91
	2

	91026
	15
	9.3
	90
	2

	91026
	16
	9.3
	87
	7

	91026
	17
	8.3
	82
	10

	91026
	18
	8.0
	77
	15

	91026
	19
	8.1
	73
	21

	91026
	20
	8.1
	71
	29

	91026
	21
	7.4
	69
	37

	91026
	22
	7.1
	65
	43

	91026
	23
	7.2
	62
	48

	91026
	24
	7.6
	61
	50

	91027
	1
	7.6
	59
	51

	91027
	2
	7.6
	59
	50

	91027
	3
	7.3
	57
	56

	91027
	4
	7.1
	56
	59

	91027
	5
	7.0
	54
	62

	91027
	6
	7.1
	56
	59

	91027
	7
	6.7
	55
	59

	91027
	8
	6.9
	57
	58

	91027
	9
	6.8
	63
	62

	91027
	10
	6.8
	67
	64

	91027
	11
	6.9
	70
	59

	91027
	12
	7.0
	71
	53

	91027
	13
	7.1
	74
	39

	91027
	14
	8.1
	77
	9

	91027
	15
	8.6
	74
	9

	91027
	16
	8.3
	71
	9

	91027
	17
	8.1
	69
	9

	91027
	18
	7.8
	66
	9

	91027
	19
	8.4
	65
	10

	91027
	20
	8.7
	64
	16

	91027
	21
	8.7
	62
	24

	91027
	22
	8.5
	61
	27

	91027
	23
	8.7
	59
	28

	91027
	24
	8.7
	58
	28

	91028
	1
	8.9
	57
	29

	91028
	2
	8.9
	56
	30

	91028
	3
	7.9
	55
	29

	91028
	4
	7.5
	55
	28

	91028
	5
	7.9
	55
	25

	91028
	6
	8.0
	55
	21

	91028
	7
	7.9
	55
	20

	91028
	8
	8.1
	58
	17

	91028
	9
	7.7
	60
	13

	91028
	10
	7.7
	62
	10

	91028
	11
	7.8
	64
	7

	91028
	12
	7.7
	65
	6

	91028
	13
	7.9
	67
	4

	91028
	14
	7.8
	69
	3

	91028
	15
	8.1
	70
	3

	91028
	16
	8.2
	70
	3

	91028
	17
	7.8
	67
	6

	91028
	18
	7.9
	64
	10

	91028
	19
	8.0
	61
	11

	91028
	20
	7.9
	59
	12

	91028
	21
	8.0
	58
	14

	91028
	22
	7.8
	58
	17

	91028
	23
	7.7
	58
	19

	91028
	24
	7.7
	58
	20

	91029
	1
	7.7
	57
	21

	91029
	2
	7.7
	55
	23

	91029
	3
	7.8
	51
	29

	91029
	4
	7.7
	48
	36

	91029
	5
	7.8
	47
	40

	91029
	6
	7.7
	45
	46

	91029
	7
	7.4
	45
	46

	91029
	8
	7.4
	50
	40

	91029
	9
	7.3
	57
	29

	91029
	10
	7.3
	64
	20

	91029
	11
	7.3
	68
	11

	91029
	12
	7.6
	69
	9

	91029
	13
	7.7
	71
	7

	91029
	14
	7.7
	72
	6

	91029
	15
	7.8
	72
	6

	91029
	16
	7.8
	70
	10

	91029
	17
	7.9
	66
	18

	91029
	18
	7.8
	63
	28

	91029
	19
	7.7
	59
	43

	91029
	20
	7.4
	57
	48

	91029
	21
	7.7
	55
	54

	91029
	22
	7.5
	54
	56

	91029
	23
	7.8
	53
	57

	91029
	24
	7.7
	52
	58

	91030
	1
	7.4
	51
	60

	91030
	2
	7.6
	50
	60

	91030
	3
	7.5
	49
	59

	91030
	4
	7.3
	48
	60

	91030
	5
	7.1
	48
	60

	91030
	6
	7.1
	47
	59

	91030
	7
	7.0
	48
	57

	91030
	8
	7.2
	53
	48

	91030
	9
	7.2
	60
	38

	91030
	10
	7.2
	67
	28

	91030
	11
	7.1
	70
	24

	91030
	12
	7.4
	72
	20

	91030
	13
	7.5
	74
	18

	91030
	14
	7.7
	76
	19

	91030
	15
	7.6
	76
	23

	91030
	16
	7.5
	74
	28

	91030
	17
	7.5
	70
	31

	91030
	18
	7.6
	66
	37

	91030
	19
	7.6
	63
	46

	91030
	20
	7.4
	61
	52

	91030
	21
	7.3
	58
	53

	91030
	22
	7.1
	55
	58

	91030
	23
	7.2
	54
	64

	91030
	24
	7.0
	53
	67

	91101
	1
	7.4
	56
	60

	91101
	2
	7.6
	56
	61

	91101
	3
	7.5
	54
	62

	91101
	4
	7.5
	54
	60

	91101
	5
	7.5
	53
	62

	91101
	6
	7.4
	52
	63

	91101
	7
	7.4
	53
	62

	91101
	8
	7.3
	58
	56

	91101
	9
	7.2
	66
	45

	91101
	10
	7.3
	77
	25

	91101
	11
	7.5
	82
	18

	91101
	12
	7.6
	85
	17

	91101
	13
	7.6
	86
	14

	91101
	14
	7.8
	87
	12

	91101
	15
	7.9
	88
	12

	91101
	16
	7.9
	86
	22

	91101
	17
	7.8
	80
	33

	91101
	18
	7.7
	74
	37

	91101
	19
	7.8
	70
	37

	91101
	20
	7.5
	66
	42

	91101
	21
	7.7
	62
	50

	91101
	22
	7.5
	60
	50

	91101
	23
	7.5
	59
	50

	91101
	24
	7.4
	57
	53

	91103
	1
	6.9
	55
	75

	91103
	2
	6.8
	54
	75

	91103
	3
	6.7
	54
	80

	91103
	4
	7.0
	53
	77

	91103
	5
	7.1
	53
	75

	91103
	6
	7.2
	53
	71

	91103
	7
	7.2
	52
	73

	91103
	8
	7.0
	58
	63

	91103
	9
	7.5
	65
	52

	91103
	10
	8.0
	71
	43

	91103
	11
	7.9
	76
	36

	91103
	12
	8.2
	82
	24

	91103
	13
	8.3
	86
	19

	91103
	14
	8.7
	87
	21

	91103
	15
	8.8
	85
	31

	91103
	16
	7.8
	83
	32

	91103
	17
	7.3
	77
	34

	91103
	18
	7.4
	67
	60

	91103
	19
	7.2
	63
	73

	91103
	20
	7.0
	61
	77

	91103
	21
	7.2
	60
	80

	91103
	22
	7.4
	58
	81

	91103
	23
	7.5
	56
	80

	91103
	24
	7.6
	55
	81

	91104
	1
	7.3
	54
	85

	91104
	2
	7.5
	53
	86

	91104
	3
	7.2
	53
	87

	91104
	4
	7.2
	55
	89

	91104
	5
	6.9
	55
	89

	91104
	6
	6.9
	55
	89

	91104
	7
	7.0
	54
	89

	91104
	8
	7.0
	54
	89

	91104
	9
	6.8
	59
	88

	91104
	10
	6.9
	64
	70

	91104
	11
	7.0
	68
	62

	91104
	12
	7.2
	71
	54

	91104
	13
	7.3
	73
	51

	91104
	14
	7.0
	73
	49

	91104
	15
	7.2
	73
	51

	91104
	16
	7.0
	72
	53

	91104
	17
	7.1
	69
	58

	91104
	18
	6.9
	64
	68

	91104
	19
	7.1
	61
	74

	91104
	20
	7.1
	60
	76

	91104
	21
	7.2
	59
	79

	91104
	22
	6.8
	58
	81

	91104
	23
	6.8
	57
	83

	91104
	24
	6.8
	57
	85

	91105
	1
	6.9
	57
	85

	91105
	2
	6.6
	57
	84

	91105
	3
	6.6
	58
	82

	91105
	4
	6.8
	58
	82

	91105
	5
	6.7
	58
	80

	91105
	6
	6.3
	58
	79

	91105
	7
	6.6
	58
	77

	91105
	8
	6.9
	59
	74

	91105
	9
	6.9
	61
	71

	91105
	10
	6.9
	62
	68

	91105
	11
	7.4
	66
	60

	91105
	12
	7.1
	68
	56

	91105
	13
	7.4
	70
	52

	91105
	14
	7.3
	71
	49

	91105
	15
	8.0
	70
	53

	91105
	16
	7.9
	68
	56

	91105
	17
	7.4
	65
	62

	91105
	18
	7.6
	62
	68

	91105
	19
	7.2
	61
	73

	91105
	20
	7.2
	60
	75

	91105
	21
	7.4
	59
	77

	91105
	22
	7.6
	58
	80

	91105
	23
	7.6
	58
	80

	91105
	24
	7.2
	56
	83

	91108
	1
	6.9
	58
	82

	91108
	2
	6.9
	57
	81

	91108
	3
	7.1
	57
	81

	91108
	4
	7.1
	57
	81

	91108
	5
	7.0
	57
	80

	91108
	6
	6.9
	56
	80

	91108
	7
	6.9
	56
	81

	91108
	8
	7.1
	57
	80

	91108
	9
	7.0
	58
	78

	91108
	10
	7.4
	62
	71

	91108
	11
	7.1
	66
	63

	91108
	12
	7.2
	69
	57

	91108
	13
	6.9
	72
	49

	91108
	14
	7.3
	73
	45

	91108
	15
	7.4
	74
	45

	91108
	16
	7.5
	72
	52

	91108
	17
	7.3
	67
	59

	91108
	18
	7.5
	63
	67

	91108
	19
	8.0
	61
	71

	91108
	20
	7.4
	59
	73

	91108
	21
	7.3
	57
	78

	91108
	22
	7.0
	55
	80

	91108
	23
	7.2
	54
	82

	91108
	24
	7.3
	53
	83

	91109
	1
	7.2
	53
	85

	91109
	2
	7.5
	52
	84

	91109
	3
	7.6
	52
	84

	91109
	4
	7.5
	51
	83

	91109
	5
	7.1
	51
	83

	91109
	6
	7.2
	50
	82

	91109
	7
	7.3
	49
	82

	91109
	8
	7.5
	52
	75

	91109
	9
	7.3
	57
	68

	91109
	10
	7.1
	66
	56

	91109
	11
	7.0
	69
	48

	91109
	12
	7.3
	75
	39

	91109
	13
	7.6
	78
	30

	91109
	14
	7.7
	80
	25

	91109
	15
	7.5
	79
	37

	91109
	16
	7.2
	78
	37

	91109
	17
	7.1
	74
	40

	91109
	18
	7.2
	69
	51

	91109
	19
	6.9
	66
	59

	91109
	20
	7.1
	63
	66

	91109
	21
	6.9
	61
	70

	91109
	22
	7.0
	59
	72

	91109
	23
	7.2
	56
	75

	91109
	24
	7.1
	55
	72

	91111
	1
	7.5
	61
	55

	91111
	2
	7.7
	61
	55

	91111
	3
	7.7
	60
	57

	91111
	4
	7.8
	60
	61

	91111
	5
	7.8
	60
	60

	91111
	6
	7.8
	59
	60

	91111
	7
	7.8
	59
	62

	91111
	8
	7.8
	61
	59

	91111
	9
	7.7
	67
	44

	91111
	10
	7.7
	71
	35

	91111
	11
	7.6
	73
	35

	91111
	12
	7.6
	76
	31

	91111
	13
	7.7
	77
	28

	91111
	14
	7.7
	79
	24

	91111
	15
	7.7
	77
	31

	91111
	16
	7.6
	74
	39

	91111
	17
	7.9
	70
	39

	91111
	18
	7.8
	67
	40

	91111
	19
	7.4
	64
	42

	91111
	20
	7.6
	62
	49

	91111
	21
	7.3
	59
	53

	91111
	22
	7.3
	58
	58

	91111
	23
	7.3
	57
	57

	91111
	24
	7.3
	56
	58

	91112
	1
	7.5
	55
	67

	91112
	2
	7.5
	54
	72

	91112
	3
	7.4
	53
	69

	91112
	4
	7.7
	53
	64

	91112
	5
	7.8
	53
	69

	91112
	6
	7.8
	53
	70

	91112
	7
	7.6
	53
	69

	91112
	8
	7.6
	55
	65

	91112
	9
	7.4
	61
	50

	91112
	10
	7.5
	68
	35

	91112
	11
	7.6
	71
	30

	91112
	12
	7.6
	70
	36

	91112
	13
	7.6
	70
	46

	91112
	14
	7.5
	69
	45

	91112
	15
	7.5
	68
	50

	91112
	16
	7.6
	67
	57

	91112
	17
	7.4
	65
	62

	91112
	18
	7.5
	63
	71

	91112
	19
	7.4
	62
	76

	91112
	20
	7.4
	62
	76

	91112
	21
	7.4
	61
	76

	91112
	22
	7.4
	60
	78

	91112
	23
	7.4
	60
	80

	91112
	24
	7.4
	59
	82

	91113
	1
	7.4
	58
	81

	91113
	2
	7.4
	57
	83

	91113
	3
	7.6
	58
	84

	91113
	4
	7.5
	58
	85

	91113
	5
	7.4
	57
	87

	91113
	6
	7.4
	55
	88

	91113
	7
	7.5
	55
	88

	91113
	8
	7.5
	56
	87

	91113
	9
	7.1
	60
	76

	91113
	10
	7.2
	63
	67

	91113
	11
	7.2
	65
	59

	91113
	12
	7.2
	67
	54

	91113
	13
	7.3
	69
	41

	91113
	14
	7.6
	70
	31

	91113
	15
	7.7
	68
	39

	91113
	16
	7.6
	66
	46

	91113
	17
	7.5
	63
	48

	91113
	18
	7.5
	61
	49

	91113
	19
	7.6
	59
	51

	91113
	20
	7.5
	56
	56

	91113
	21
	7.3
	53
	61

	91113
	22
	7.4
	53
	63

	91113
	23
	7.3
	53
	64

	91113
	24
	7.3
	51
	68

	91117
	1
	8.2
	53
	38

	91117
	2
	8.2
	51
	40

	91117
	3
	8.2
	49
	45

	91117
	4
	7.8
	48
	47

	91117
	5
	7.5
	47
	49

	91117
	6
	7.6
	47
	49

	91117
	7
	7.7
	47
	49

	91117
	8
	7.6
	50
	48

	91117
	9
	7.9
	59
	34

	91117
	10
	7.9
	68
	18

	91117
	11
	7.8
	75
	10

	91117
	12
	8.6
	79
	5

	91117
	13
	8.9
	82
	4

	91117
	14
	9.0
	83
	4

	91117
	15
	9.0
	80
	12

	91117
	16
	9.0
	74
	21

	91117
	17
	8.9
	69
	23

	91117
	18
	9.3
	65
	30

	91117
	19
	8.4
	62
	40

	91117
	20
	8.0
	60
	46

	91117
	21
	8.0
	58
	51

	91117
	22
	8.1
	54
	58

	91117
	23
	7.8
	53
	61

	91117
	24
	7.8
	51
	63

	91119
	1
	7.1
	50
	83

	91119
	2
	6.9
	49
	82

	91119
	3
	7.0
	48
	83

	91119
	4
	7.1
	47
	82

	91119
	5
	7.2
	46
	83

	91119
	6
	7.2
	45
	83

	91119
	7
	7.0
	45
	80

	91119
	8
	7.2
	48
	78

	91119
	9
	7.1
	55
	66

	91119
	10
	7.1
	61
	50

	91119
	11
	7.2
	67
	38

	91119
	12
	7.2
	74
	27

	91119
	13
	7.5
	77
	20

	91119
	14
	7.6
	79
	15

	91119
	15
	7.6
	79
	18

	91119
	16
	7.6
	76
	28

	91119
	17
	7.5
	72
	28

	91119
	18
	7.6
	66
	39

	91119
	19
	7.7
	60
	46

	91119
	20
	7.5
	57
	53

	91119
	21
	7.2
	55
	57

	91119
	22
	7.3
	53
	61

	91119
	23
	7.3
	52
	61

	91119
	24
	7.2
	51
	62

	91120
	1
	7.4
	51
	61

	91120
	2
	7.3
	49
	64

	91120
	3
	7.3
	48
	67

	91120
	4
	7.2
	46
	69

	91120
	5
	7.3
	45
	69

	91120
	6
	6.9
	45
	68

	91120
	7
	7.2
	46
	65

	91120
	8
	7.2
	49
	57

	91120
	9
	7.6
	57
	45

	91120
	10
	7.3
	61
	47

	91120
	11
	6.9
	64
	48

	91120
	12
	6.9
	67
	47

	91120
	13
	6.9
	70
	40

	91120
	14
	7.1
	70
	40

	91120
	15
	7.3
	70
	48

	91120
	16
	7.3
	68
	51

	91120
	17
	7.3
	65
	60

	91120
	18
	7.2
	62
	68

	91120
	19
	7.3
	60
	72

	91120
	20
	7.1
	58
	78

	91120
	21
	7.0
	56
	80

	91120
	22
	7.0
	55
	82

	91120
	23
	7.2
	52
	81

	91120
	24
	7.1
	51
	80

	91122
	1
	7.2
	49
	83

	91122
	2
	7.3
	49
	83

	91122
	3
	7.4
	48
	83

	91122
	4
	7.1
	47
	84

	91122
	5
	7.1
	46
	85

	91122
	6
	7.2
	45
	84

	91122
	7
	7.3
	45
	85

	91122
	8
	7.1
	48
	80

	91122
	9
	6.9
	54
	73

	91122
	10
	6.8
	61
	62

	91122
	11
	6.8
	64
	55

	91122
	12
	7.1
	67
	47

	91122
	13
	7.3
	70
	36

	91122
	14
	7.4
	70
	34

	91122
	15
	7.6
	71
	35

	91122
	16
	7.5
	69
	37

	91122
	17
	7.5
	64
	45

	91122
	18
	7.5
	61
	51

	91122
	19
	7.5
	58
	58

	91122
	20
	7.4
	54
	62

	91122
	21
	7.4
	52
	66

	91122
	22
	7.4
	51
	63

	91122
	23
	7.2
	51
	69

	91122
	24
	7.3
	49
	73

	91123
	1
	7.3
	48
	77

	91123
	2
	7.2
	47
	77

	91123
	3
	7.1
	47
	78

	91123
	4
	7.2
	46
	79

	91123
	5
	7.3
	46
	78

	91123
	6
	7.2
	45
	79

	91123
	7
	7.4
	45
	78

	91123
	8
	7.4
	48
	73

	91123
	9
	7.5
	54
	66

	91123
	10
	7.1
	62
	53

	91123
	11
	7.1
	69
	38

	91123
	12
	7.1
	74
	29

	91123
	13
	7.2
	78
	22

	91123
	14
	7.5
	80
	18

	91123
	15
	7.5
	81
	14

	91123
	16
	8.5
	80
	15

	91123
	17
	8.4
	75
	27

	91123
	18
	7.8
	68
	49

	91123
	19
	8.2
	64
	53

	91123
	20
	7.9
	62
	59

	91123
	21
	8.0
	58
	62

	91123
	22
	7.9
	55
	63

	91123
	23
	7.9
	54
	67

	91123
	24
	7.6
	53
	65

	91124
	1
	7.9
	52
	64

	91124
	2
	8.2
	50
	69

	91124
	3
	8.5
	49
	69

	91124
	4
	8.2
	47
	68

	91124
	5
	8.2
	47
	66

	91124
	6
	8.2
	46
	65

	91124
	7
	8.6
	46
	63

	91124
	8
	8.7
	49
	58

	91124
	9
	8.2
	56
	48

	91124
	10
	8.2
	65
	27

	91124
	11
	8.2
	72
	14

	91124
	12
	7.9
	74
	12

	91124
	13
	7.9
	75
	11

	91124
	14
	8.0
	77
	10

	91124
	15
	7.8
	78
	7

	91124
	16
	8.3
	77
	9

	91124
	17
	8.3
	72
	11

	91124
	18
	8.3
	65
	17

	91124
	19
	8.6
	60
	22

	91124
	20
	8.5
	57
	27

	91124
	21
	8.6
	56
	31

	91124
	22
	8.4
	54
	41

	91124
	23
	8.2
	52
	45

	91124
	24
	8.1
	51
	46

	91126
	1
	7.6
	51
	45

	91126
	2
	7.4
	51
	43

	91126
	3
	7.4
	50
	44

	91126
	4
	7.5
	49
	45

	91126
	5
	7.6
	47
	49

	91126
	6
	7.3
	47
	47

	91126
	7
	7.3
	47
	46

	91126
	8
	7.3
	50
	43

	91126
	9
	7.5
	59
	31

	91126
	10
	7.5
	68
	19

	91126
	11
	7.4
	74
	14

	91126
	12
	7.5
	79
	9

	91126
	13
	7.7
	83
	6

	91126
	14
	7.8
	85
	5

	91126
	15
	8.1
	86
	3

	91126
	16
	8.2
	86
	3

	91126
	17
	8.0
	79
	10

	91126
	18
	7.8
	72
	17

	91126
	19
	7.8
	66
	21

	91126
	20
	7.7
	61
	29

	91126
	21
	7.7
	59
	33

	91126
	22
	7.6
	56
	39

	91126
	23
	7.7
	55
	41

	91126
	24
	7.8
	54
	41

	91130
	1
	7.7
	49
	59

	91130
	2
	7.6
	47
	63

	91130
	3
	7.8
	47
	61

	91130
	4
	7.8
	46
	61

	91130
	5
	7.9
	45
	60

	91130
	6
	7.8
	44
	61

	91130
	7
	7.8
	44
	61

	91130
	8
	7.8
	48
	53

	91130
	9
	7.9
	55
	44

	91130
	10
	7.9
	66
	28

	91130
	11
	8.0
	72
	15

	91130
	12
	8.0
	75
	8

	91130
	13
	7.9
	76
	8

	91130
	14
	8.0
	77
	7

	91130
	15
	8.0
	77
	7

	91130
	16
	7.9
	77
	9

	91130
	17
	8.3
	72
	14

	91130
	18
	8.4
	64
	24

	91130
	19
	8.5
	60
	31

	91130
	20
	8.7
	57
	33

	91130
	21
	8.2
	55
	38

	91130
	22
	7.9
	54
	39

	91130
	23
	8.4
	52
	42

	91130
	24
	8.2
	51
	43

	91201
	1
	7.6
	50
	42

	91201
	2
	7.8
	49
	46

	91201
	3
	7.6
	47
	50

	91201
	4
	7.5
	45
	54

	91201
	5
	7.4
	45
	53

	91201
	6
	7.4
	46
	51

	91201
	7
	7.4
	44
	53

	91201
	8
	7.5
	48
	47

	91201
	9
	7.8
	54
	38

	91201
	10
	8.5
	61
	44

	91201
	11
	7.5
	65
	55

	91201
	12
	7.2
	66
	53

	91201
	13
	7.1
	67
	51

	91201
	14
	7.2
	66
	54

	91201
	15
	7.3
	66
	51

	91201
	16
	7.9
	63
	58

	91201
	17
	7.7
	60
	65

	91201
	18
	7.4
	58
	71

	91201
	19
	7.5
	57
	75

	91201
	20
	7.5
	57
	75

	91201
	21
	7.4
	57
	74

	91201
	22
	7.4
	56
	72

	91201
	23
	7.4
	56
	69

	91201
	24
	7.4
	55
	71

	91203
	1
	7.5
	48
	84

	91203
	2
	7.9
	48
	84

	91203
	3
	7.6
	47
	83

	91203
	4
	7.6
	45
	85

	91203
	5
	7.6
	45
	84

	91203
	6
	7.4
	44
	83

	91203
	7
	7.0
	46
	81

	91203
	8
	7.0
	48
	78

	91203
	9
	6.7
	51
	74

	91203
	10
	7.0
	58
	66

	91203
	11
	7.2
	61
	57

	91203
	12
	7.5
	64
	53

	91203
	13
	7.2
	66
	48

	91203
	14
	7.5
	67
	46

	91203
	15
	6.8
	67
	45

	91203
	16
	8.4
	64
	55

	91203
	17
	7.1
	59
	67

	91203
	18
	7.2
	56
	74

	91203
	19
	7.1
	55
	76

	91203
	20
	7.1
	53
	78

	91203
	21
	7.0
	51
	80

	91203
	22
	6.9
	49
	82

	91203
	23
	6.9
	48
	84

	91203
	24
	7.0
	47
	85

	91204
	1
	6.9
	46
	84

	91204
	2
	7.0
	46
	84

	91204
	3
	6.8
	45
	82

	91204
	4
	7.3
	45
	81

	91204
	5
	7.7
	44
	82

	91204
	6
	7.7
	44
	82

	91204
	7
	7.8
	43
	75

	91204
	8
	7.8
	45
	68

	91204
	9
	7.3
	51
	60

	91204
	10
	7.0
	57
	41

	91204
	11
	7.2
	64
	21

	91204
	12
	10.6
	68
	13

	91204
	13
	7.2
	72
	12

	91204
	14
	7.7
	72
	11

	91204
	15
	8.2
	73
	11

	91204
	16
	8.1
	72
	12

	91204
	17
	8.3
	65
	37

	91204
	18
	7.9
	59
	59

	91204
	19
	7.8
	57
	67

	91204
	20
	7.5
	56
	68

	91204
	21
	7.2
	55
	73

	91204
	22
	6.9
	53
	75

	91204
	23
	7.1
	50
	80

	91204
	24
	7.4
	48
	75

	91205
	1
	7.1
	48
	74

	91205
	2
	7.1
	47
	72

	91205
	3
	7.2
	47
	69

	91205
	4
	7.3
	46
	69

	91205
	5
	7.2
	44
	73

	91205
	6
	6.9
	45
	71

	91205
	7
	7.0
	46
	69

	91205
	8
	7.4
	46
	62

	91205
	9
	7.2
	48
	60

	91205
	10
	7.3
	53
	61

	91205
	11
	7.2
	58
	62

	91205
	12
	6.9
	58
	62

	91205
	13
	6.8
	59
	59

	91205
	14
	7.0
	60
	56

	91205
	15
	7.1
	59
	60

	91205
	16
	6.9
	58
	60

	91205
	17
	7.0
	56
	62

	91205
	18
	7.0
	55
	65

	91205
	19
	7.2
	54
	72

	91205
	20
	7.2
	54
	70

	91205
	21
	7.4
	54
	69

	91205
	22
	7.1
	53
	71

	91205
	23
	7.1
	54
	69

	91205
	24
	7.1
	53
	67

	91206
	1
	7.1
	52
	68

	91206
	2
	7.0
	50
	71

	91206
	3
	7.3
	49
	74

	91206
	4
	7.3
	50
	72

	91206
	5
	7.0
	50
	72

	91206
	6
	7.1
	49
	73

	91206
	7
	7.0
	46
	78

	91206
	8
	6.9
	47
	74

	91206
	9
	6.9
	52
	63

	91206
	10
	6.9
	56
	52

	91206
	11
	6.8
	57
	48

	91206
	12
	7.0
	56
	47

	91206
	13
	7.1
	56
	46

	91206
	14
	7.2
	57
	45

	91206
	15
	7.2
	57
	47

	91206
	16
	7.3
	56
	49

	91206
	17
	7.2
	54
	53

	91206
	18
	7.2
	53
	56

	91206
	19
	7.3
	52
	60

	91206
	20
	7.4
	50
	64

	91206
	21
	7.4
	50
	65

	91206
	22
	7.3
	50
	65

	91206
	23
	7.1
	50
	63

	91206
	24
	7.2
	51
	60

	91208
	1
	8.1
	43
	47

	91208
	2
	7.9
	41
	54

	91208
	3
	7.8
	40
	55

	91208
	4
	7.7
	37
	63

	91208
	5
	7.6
	36
	68

	91208
	6
	7.6
	35
	70

	91208
	7
	7.4
	34
	73

	91208
	8
	7.6
	37
	68

	91208
	9
	7.4
	43
	56

	91208
	10
	7.3
	48
	42

	91208
	11
	7.4
	52
	37

	91208
	12
	7.5
	53
	35

	91208
	13
	7.8
	55
	33

	91208
	14
	8.1
	56
	31

	91208
	15
	7.9
	56
	30

	91208
	16
	7.5
	55
	30

	91208
	17
	8.0
	52
	40

	91208
	18
	7.9
	49
	45

	91208
	19
	8.0
	47
	51

	91208
	20
	8.5
	44
	57

	91208
	21
	8.5
	42
	63

	91208
	22
	8.6
	41
	67

	91208
	23
	8.2
	42
	64

	91208
	24
	8.1
	41
	67

	91209
	1
	8.2
	41
	68

	91209
	2
	8.2
	42
	64

	91209
	3
	8.2
	45
	58

	91209
	4
	8.2
	45
	58

	91209
	5
	8.1
	44
	61

	91209
	6
	8.3
	42
	65

	91209
	7
	8.1
	41
	69

	91209
	8
	8.1
	42
	67

	91209
	9
	8.1
	46
	59

	91209
	10
	7.8
	50
	52

	91209
	11
	7.5
	53
	45

	91209
	12
	7.9
	56
	39

	91209
	13
	7.8
	58
	30

	91209
	14
	8.0
	58
	31

	91209
	15
	7.8
	60
	30

	91209
	16
	8.0
	59
	31

	91209
	17
	7.8
	55
	38

	91209
	18
	7.8
	52
	53

	91209
	19
	7.1
	51
	59

	91209
	20
	7.4
	48
	65

	91209
	21
	7.5
	45
	70

	91209
	22
	7.3
	44
	74

	91209
	23
	7.5
	43
	75

	91209
	24
	7.7
	42
	75

	91211
	1
	7.2
	49
	79

	91211
	2
	6.8
	49
	83

	91211
	3
	6.9
	49
	84

	91211
	4
	6.9
	49
	79

	91211
	5
	7.0
	49
	80

	91211
	6
	6.8
	50
	77

	91211
	7
	7.1
	50
	77

	91211
	8
	7.0
	50
	82

	91211
	9
	6.7
	50
	82

	91211
	10
	6.9
	52
	79

	91211
	11
	7.0
	53
	77

	91211
	12
	7.0
	54
	75

	91211
	13
	7.0
	55
	73

	91211
	14
	6.8
	57
	72

	91211
	15
	7.0
	55
	81

	91211
	16
	7.3
	54
	85

	91211
	17
	7.4
	54
	85

	91211
	18
	7.3
	54
	85

	91211
	19
	7.5
	54
	82

	91211
	20
	7.5
	52
	84

	91211
	21
	7.7
	52
	86

	91211
	22
	7.6
	52
	86

	91211
	23
	7.6
	53
	86

	91211
	24
	7.6
	53
	87

	91212
	1
	7.4
	53
	87

	91212
	2
	7.6
	53
	87

	91212
	3
	7.4
	54
	87

	91212
	4
	7.4
	54
	87

	91212
	5
	7.4
	54
	87

	91212
	6
	7.3
	55
	86

	91212
	7
	7.4
	56
	86

	91212
	8
	7.3
	56
	84

	91212
	9
	7.3
	56
	84

	91212
	10
	7.2
	57
	83

	91212
	11
	7.0
	58
	83

	91212
	12
	6.8
	59
	83

	91212
	13
	6.6
	60
	83

	91212
	14
	6.9
	61
	82

	91212
	15
	7.2
	60
	81

	91212
	16
	7.2
	59
	86

	91212
	17
	7.1
	58
	88

	91212
	18
	7.2
	59
	88

	91212
	19
	7.3
	59
	87

	91212
	20
	7.2
	59
	88

	91212
	21
	7.4
	59
	88

	91212
	22
	7.4
	59
	85

	91212
	23
	7.5
	58
	81

	91212
	24
	7.5
	56
	79

	91213
	1
	7.4
	55
	82

	91213
	2
	7.2
	55
	82

	91213
	3
	7.2
	54
	83

	91213
	4
	7.1
	53
	84

	91213
	5
	7.0
	53
	86

	91213
	6
	7.0
	53
	86

	91213
	7
	7.2
	52
	86

	91213
	8
	7.2
	51
	86

	91213
	9
	7.1
	54
	84

	91213
	10
	7.1
	55
	83

	91213
	11
	6.8
	59
	72

	91213
	12
	7.0
	61
	57

	91213
	13
	7.1
	61
	52

	91213
	14
	7.3
	61
	54

	91213
	15
	7.2
	61
	56

	91213
	16
	7.2
	60
	60

	91213
	17
	7.3
	57
	67

	91213
	18
	7.2
	57
	68

	91213
	19
	7.2
	56
	69

	91213
	20
	7.3
	56
	73

	91213
	21
	7.2
	56
	68

	91213
	22
	7.5
	54
	70

	91213
	23
	7.6
	52
	76

	91213
	24
	7.6
	50
	81

	91214
	1
	7.4
	48
	83

	91214
	2
	7.2
	47
	85

	91214
	3
	7.2
	47
	85

	91214
	4
	7.2
	46
	86

	91214
	5
	7.2
	45
	86

	91214
	6
	7.0
	45
	86

	91214
	7
	7.1
	45
	86

	91214
	8
	7.1
	46
	85

	91214
	9
	7.1
	49
	81

	91214
	10
	6.9
	55
	74

	91214
	11
	6.6
	58
	68

	91214
	12
	6.6
	61
	58

	91214
	13
	6.6
	62
	55

	91214
	14
	6.8
	63
	52

	91214
	15
	6.9
	63
	50

	91214
	16
	6.9
	63
	50

	91214
	17
	7.1
	60
	60

	91214
	18
	7.1
	57
	68

	91214
	19
	7.3
	55
	72

	91214
	20
	7.2
	53
	76

	91214
	21
	7.3
	50
	81

	91214
	22
	7.5
	49
	82

	91214
	23
	7.5
	48
	84

	91214
	24
	7.6
	48
	83

	91215
	1
	7.7
	47
	83

	91215
	2
	7.6
	45
	85

	91215
	3
	7.3
	46
	85

	91215
	4
	7.5
	46
	82

	91215
	5
	7.0
	45
	80

	91215
	6
	7.4
	44
	78

	91215
	7
	7.6
	44
	75

	91215
	8
	7.6
	48
	70

	91215
	9
	7.6
	53
	59

	91215
	10
	7.3
	58
	53

	91215
	11
	7.4
	61
	47

	91215
	12
	7.4
	63
	42

	91215
	13
	7.6
	68
	31

	91215
	14
	7.9
	71
	26

	91215
	15
	7.9
	72
	24

	91215
	16
	8.1
	69
	27

	91215
	17
	8.0
	65
	37

	91215
	18
	7.8
	61
	47

	91215
	19
	7.8
	57
	56

	91215
	20
	7.9
	55
	59

	91215
	21
	7.4
	54
	61

	91215
	22
	7.5
	54
	56

	91215
	23
	7.5
	54
	57

	91215
	24
	7.6
	52
	58

	91217
	1
	7.4
	51
	58

	91217
	2
	7.0
	50
	58

	91217
	3
	7.1
	49
	59

	91217
	4
	7.2
	49
	59

	91217
	5
	7.5
	49
	57

	91217
	6
	7.5
	48
	58

	91217
	7
	7.4
	48
	59

	91217
	8
	7.7
	50
	56

	91217
	9
	8.1
	57
	44

	91217
	10
	7.1
	63
	35

	91217
	11
	7.0
	66
	30

	91217
	12
	7.5
	71
	27

	91217
	13
	7.7
	76
	20

	91217
	14
	7.9
	77
	19

	91217
	15
	8.3
	78
	17

	91217
	16
	8.3
	78
	16

	91217
	17
	8.4
	72
	25

	91217
	18
	8.6
	64
	38

	91217
	19
	8.0
	60
	42

	91217
	20
	7.8
	59
	46

	91217
	21
	7.9
	57
	52

	91217
	22
	7.7
	56
	53

	91217
	23
	7.8
	55
	53

	91217
	24
	7.8
	55
	52

	91219
	1
	7.8
	52
	60

	91219
	2
	7.7
	51
	62

	91219
	3
	7.8
	50
	63

	91219
	4
	7.6
	49
	64

	91219
	5
	7.7
	48
	65

	91219
	6
	7.7
	48
	63

	91219
	7
	7.6
	48
	63

	91219
	8
	7.7
	50
	60

	91219
	9
	7.5
	55
	52

	91219
	10
	7.7
	61
	46

	91219
	11
	7.7
	69
	34

	91219
	12
	7.9
	75
	24

	91219
	13
	8.2
	78
	16

	91219
	14
	8.4
	80
	14

	91219
	15
	8.5
	79
	13

	91219
	16
	8.6
	78
	16

	91219
	17
	8.1
	72
	22

	91219
	18
	8.3
	66
	32

	91219
	19
	8.4
	62
	40

	91219
	20
	8.4
	61
	42

	91219
	21
	8.2
	59
	47

	91219
	22
	8.0
	58
	46

	91219
	23
	7.9
	57
	48

	91219
	24
	7.7
	57
	47

	91221
	1
	8.0
	51
	63

	91221
	2
	8.2
	50
	64

	91221
	3
	8.2
	50
	64

	91221
	4
	8.0
	49
	64

	91221
	5
	7.9
	49
	65

	91221
	6
	8.1
	49
	65

	91221
	7
	8.0
	50
	63

	91221
	8
	7.7
	50
	62

	91221
	9
	7.7
	53
	58

	91221
	10
	7.8
	57
	52

	91221
	11
	8.0
	60
	44

	91221
	12
	7.8
	64
	39

	91221
	13
	7.7
	65
	36

	91221
	14
	7.6
	65
	33

	91221
	15
	7.5
	64
	32

	91221
	16
	7.6
	63
	36

	91221
	17
	7.8
	62
	36

	91221
	18
	7.8
	61
	44

	91221
	19
	7.9
	59
	52

	91221
	20
	8.1
	57
	56

	91221
	21
	8.1
	54
	62

	91221
	22
	8.3
	52
	67

	91221
	23
	7.4
	52
	67

	91221
	24
	7.6
	52
	69

	91222
	1
	7.5
	52
	73

	91222
	2
	7.4
	52
	74

	91222
	3
	7.5
	52
	75

	91222
	4
	7.5
	52
	79

	91222
	5
	7.3
	53
	83

	91222
	6
	7.1
	53
	72

	91222
	7
	7.0
	52
	65

	91222
	8
	7.2
	52
	59

	91222
	9
	7.1
	54
	35

	91222
	10
	7.6
	54
	34

	91222
	11
	7.2
	55
	31

	91222
	12
	7.8
	58
	28

	91222
	13
	7.6
	60
	24

	91222
	14
	7.1
	60
	20

	91222
	15
	7.2
	60
	17

	91222
	16
	7.8
	59
	17

	91222
	17
	7.7
	56
	16

	91222
	18
	8.0
	54
	19

	91222
	19
	8.1
	52
	24

	91222
	20
	8.2
	51
	27

	91222
	21
	7.8
	50
	28

	91222
	22
	7.9
	50
	30

	91222
	23
	7.9
	49
	33

	91222
	24
	7.5
	48
	36

	91224
	1
	5.8
	43
	60

	91224
	2
	7.5
	41
	66

	91224
	3
	7.5
	40
	66

	91224
	4
	7.4
	39
	68

	91224
	5
	7.5
	39
	69

	91224
	6
	7.3
	38
	68

	91224
	7
	7.1
	38
	69

	91224
	8
	3.0
	39
	68

	91224
	9
	0.0
	45
	60

	91224
	10
	0.1
	51
	50

	91224
	11
	0.1
	58
	40

	91224
	12
	0.1
	63
	27

	91224
	13
	0.1
	65
	22

	91224
	14
	0.0
	67
	19

	91224
	15
	0.0
	68
	18

	91224
	19
	0.0
	54
	60

	91224
	20
	0.0
	51
	69

	91224
	21
	0.0
	48
	75

	91224
	22
	0.0
	46
	78

	91224
	23
	0.0
	45
	76

	91224
	24
	0.1
	44
	71

	91226
	1
	1.9
	46
	77

	91226
	2
	0.1
	44
	78

	91226
	3
	0.1
	42
	80

	91226
	4
	0.1
	41
	82

	91226
	5
	0.1
	40
	84

	91226
	6
	0.1
	39
	83

	91226
	7
	0.1
	40
	81

	91226
	8
	13.2
	43
	77

	91226
	9
	17.6
	47
	73

	91226
	10
	9.2
	50
	65

	91226
	11
	6.1
	52
	60

	91226
	12
	5.9
	55
	59

	91226
	13
	6.6
	56
	58

	91226
	14
	6.9
	57
	56

	91226
	15
	7.2
	59
	52

	91226
	16
	7.2
	61
	46

	91226
	17
	7.4
	58
	48

	91226
	18
	7.6
	53
	59

	91226
	19
	7.5
	49
	67

	91226
	20
	7.4
	47
	72

	91226
	21
	7.5
	45
	77

	91226
	22
	7.4
	45
	78

	91226
	23
	7.3
	44
	77

	91226
	24
	7.3
	43
	77

	91228
	1
	7.6
	49
	49

	91228
	2
	7.6
	51
	42

	91228
	3
	7.6
	50
	45

	91228
	4
	7.7
	51
	43

	91228
	5
	7.5
	50
	42

	91228
	6
	7.6
	50
	44

	91228
	7
	7.7
	50
	43

	91228
	8
	7.7
	50
	44

	91228
	9
	7.8
	52
	41

	91228
	10
	7.9
	56
	32

	91228
	11
	8.0
	60
	27

	91228
	12
	7.8
	63
	24

	91228
	13
	7.8
	65
	22

	91228
	14
	7.9
	66
	21

	91228
	15
	7.9
	69
	19

	91228
	16
	8.1
	69
	19

	91228
	17
	8.5
	65
	25

	91228
	18
	8.5
	58
	34

	91228
	19
	8.4
	54
	40

	91228
	20
	8.3
	53
	41

	91228
	21
	8.2
	50
	51

	91228
	22
	8.1
	48
	53

	91228
	23
	7.9
	48
	54

	91228
	24
	7.9
	49
	55

	91229
	1
	7.6
	49
	53

	91229
	2
	7.7
	49
	54

	91229
	3
	7.6
	49
	54

	91229
	4
	7.7
	49
	55

	91229
	5
	7.6
	49
	55

	91229
	6
	7.6
	49
	51

	91229
	7
	7.9
	47
	54

	91229
	8
	7.8
	47
	55

	91229
	9
	7.7
	51
	49

	91229
	10
	7.7
	56
	46

	91229
	11
	7.5
	61
	56

	91229
	12
	7.5
	62
	48

	91229
	13
	7.6
	64
	42

	91229
	14
	7.5
	65
	38

	91229
	15
	7.8
	65
	41

	91229
	16
	7.8
	63
	51

	91229
	17
	7.6
	61
	51

	91229
	18
	7.6
	58
	54

	91229
	19
	7.7
	55
	63

	91229
	20
	7.5
	53
	69

	91229
	21
	7.4
	51
	76

	91229
	22
	7.0
	50
	79

	91229
	23
	7.0
	48
	81

	91229
	24
	6.9
	48
	78

	91230
	1
	7.1
	47
	78

	91230
	2
	7.2
	47
	77

	91230
	3
	7.2
	46
	80

	91230
	4
	7.2
	47
	78

	91230
	5
	7.1
	46
	78

	91230
	6
	7.3
	47
	77

	91230
	7
	7.3
	48
	75

	91230
	8
	7.3
	49
	74

	91230
	9
	7.4
	51
	71

	91230
	10
	7.2
	49
	81

	91230
	11
	7.1
	50
	84

	91230
	12
	7.2
	50
	85

	91230
	13
	7.3
	50
	84

	91230
	14
	7.0
	50
	83

	91230
	15
	7.1
	51
	83

	91230
	16
	7.1
	52
	81

	91230
	17
	7.0
	52
	80

	91230
	18
	7.1
	52
	81

	91230
	19
	7.0
	52
	82

	91230
	20
	7.1
	52
	82

	91230
	21
	7.2
	52
	82

	91230
	22
	7.4
	51
	83

	91230
	23
	7.4
	51
	84

	91230
	24
	7.3
	50
	84

	91231
	1
	7.2
	48
	86

	91231
	2
	7.2
	47
	87

	91231
	3
	7.3
	46
	87

	91231
	4
	7.4
	45
	87

	91231
	5
	7.2
	45
	87

	91231
	6
	7.2
	43
	87

	91231
	7
	7.2
	43
	87

	91231
	8
	7.1
	43
	88

	91231
	9
	7.0
	47
	88

	91231
	10
	6.8
	52
	83

	91231
	11
	6.9
	58
	62

	91231
	12
	6.9
	63
	49

	91231
	13
	6.9
	67
	35

	91231
	14
	7.2
	68
	30

	91231
	15
	7.3
	68
	29

	91231
	16
	7.3
	66
	32

	91231
	17
	7.5
	66
	35

	91231
	18
	7.6
	60
	46

	91231
	19
	7.3
	56
	55

	91231
	20
	7.2
	53
	63

	91231
	21
	7.3
	52
	64

	91231
	22
	7.2
	50
	68

	91231
	23
	7.3
	51
	64

	91231
	24
	7.2
	51
	57


Total Number of Affected Units ~1,600








� The term “sealed burners” is used to distinguish them from atmospheric burners which utilize a non-sealed combustion chamber in which natural draft is used to exhaust combustion gases.  The atmospheric burners are required to comply with a less stringent limit of 12 ppm (0.015 lbs/106 Btu).


� A Thermal fluid heater means a process heater in which a process is heated indirectly by a heated fluid other than water.


� Control Measure MSC-01, Facility Modernization, Appendix IV-A, 2007 AQMP, June 2007





AQMD

ES - 1
August 1999


